pyrose

| Employer's Requirements – General - Solar PV |  |
| --- | --- |
| Draft |  |
| Triple Power Generation Limited |  |
| December 2025 | P0049208 – rev00 |

Issue and Revision Record Rev; Date; Originator; Checker; Approver; Narrative. 00; 12/12/2025; FG011, MRA06; PANAN; FD020; Draft for Client’s input..

Disclaimer

This document has been prepared for the titled project or named part thereof and should not be relied upon or used for any other project without an independent check being carried out as to its suitability and prior written authority of RINA being obtained. RINA accepts no responsibility or liability for the consequence of this document being used for a purpose other than those for which it was commissioned. Any person using or relying on the document for such other purpose will by such use or reliance be taken to confirm his agreement to indemnify RINA for all loss or damage resulting therefrom. RINA accepts no responsibility or liability for this document to any party other than the person by whom it was commissioned.

As provided for in RINA’s proposal, to the extent that this report is based on information supplied by other parties, RINA accepts no liability for any loss or damage suffered by the client, whether contractual or tortious, stemming from any conclusions based on data supplied by parties other than RINA and used by RINA in preparing this report.

Contents

1	Introduction	8

1.1	General	8

1.2	Definitions	8

1.2.1	Abbreviations	11

1.3	Law, Permits and Standards	13

1.3.1	Technology Specific Requirements	14

1.4	General Requirements	15

2	General Scope of the Works	17

2.1	Preparatory Works	17

2.2	Infrastructure Works	17

2.3	Construction Facilities	18

2.4	Design and Engineering	18

2.5	Procurement and Delivery	18

2.6	Transportation and Logistics	19

2.7	Surveys, Studies and Reports	20

2.8	Equipment and Systems	21

2.9	Construction	21

2.9.1	Civil Works	21

2.9.2	Mechanical Works	22

2.9.3	Electrical Works	22

2.10	Parts and Tools	23

2.11	Software	24

2.12	Performances, Tests and Warranties	24

2.13	Documents	25

2.14	Training	25

2.15	Compliance	26

2.15.1	Permit Compliance	26

2.15.2	Connection Agreement	26

2.15.3	Lease Agreements	26

2.16	Quality, Health, Safety and Environment	26

2.16.1	Construction, Design and Management (CDM) Regulations 2015	27

2.17	Internal Connection Works	29

2.18	Substation and O&M Building	29

2.19	Operation and Maintenance Building	30

2.20	Earthing System	31

2.21	Lightning System and Overvoltage Protection	32

2.22	Employer Provided Equipment	32

2.23	System Design and Installation Standards	32

2.23.1	General	32

2.23.2	Earthing Standards	33

2.23.3	Overvoltage and Lightning Protection	33

2.24	Inspection and Testing of Major Components	33

2.24.1	Factory Inspection and Testing	34

2.24.2	Pre-Shipment Factory Testing and Inspection	34

2.25	Plant Commissioning Tests	35

3	Site Specific Details	37

3.1	The Site	37

3.1.1	Employer provided documents	37

3.2	Site Conditions	38

Save as regards Unforeseen Site Conditions, the Contractor shall be responsible for identifying and fully detailing all relevant Site and climatic conditions applicable to the Plant and documenting these conditions in a Site Conditions report to be submitted within four (4) weeks of the Notice to Proceed. The Contractor’s assessment shall be based on its own assessment and investigation as to the most severe climatic conditions or local regulations which should be used as a basis for the final design of the Plant.	38

3.3	Technology Specific Scope of Work	38

4	Project Management	39

4.1	Planning and Coordination	39

4.2	Procurement	40

4.3	Construction Management	40

4.4	Progress Reporting and Meetings	41

5	Quality Assurance/Quality Control (QA/QC)	42

5.1	Factory Acceptance Tests	43

5.2	Inspection and Test Plan	43

5.2.1	Notice of Inspection and Test	43

5.2.2	Records	43

6	Health and Safety Plan	45

6.1	Minimum PPE Requirements	45

6.2	Incident Reporting	46

6.3	Hazardous Areas	46

6.4	Fire Protection and Fire Fighting Systems	46

6.5	Noise Limits	47

7	Environmental Plan	49

8	Design Requirements	50

8.1	General	50

8.2	Design Review by Employer	50

8.3	Civil And Structural Works	51

8.3.1	General Characteristics	51

8.3.2	Access Roads, Parking Areas, Other Areas	52

8.3.3	Foundations	53

8.3.4	Structural Design Principles	54

8.3.5	Load Assumptions	54

8.3.6	Wind Loads	54

8.3.7	Seismic Loads	55

8.3.8	Civil Construction Material	55

8.4	HV AC Works	55

8.5	Electrical Works	55

8.5.1	P28 and P29 Modelling Package	57

9	Equipment And System Requirements	58

9.1	General	58

9.2	Labelling	58

9.3	LV/HV Transformers	59

9.4	Enclosures	60

9.5	Energy Meters	61

9.6	Electrical Protection	61

9.6.1	AC Protection and Circuits	61

9.6.2	HV Switchgear Units	61

9.6.3	LV AC Protection and Auxiliary Services	62

9.7	Lightning Protection and Earthing System	63

9.7.1	Lightning System and Overvoltage Protection	63

9.7.2	Earthing System	63

9.7.3	Equipotential Connection	64

9.8	Cable Selection, Design and Connections	64

9.8.1	Cable Sizing	65

9.8.2	DC Cables	66

9.8.3	LV AC Cables	66

9.8.4	High Voltage Cables	66

9.8.5	Communication Cables	67

9.8.6	Auxiliary Power Cables	68

9.8.7	Cable Runs and Trenches	68

9.8.8	Cable Jointing and Termination	68

9.9	UPS	69

9.10	Scada System	69

9.10.1	Key Functionalities and Requirements	69

9.10.2	Data, Events and Alarms	71

9.10.3	Data Storage	72

9.10.4	Weather Stations	72

9.11	Security System	73

9.11.1	Fence and Gate	73

9.11.2	Security During the Construction Phase	73

9.11.3	Permanent Security Arrangements	74

9.12	Lighting	74

9.13	Temporary Site Facilities	75

9.13.1	Facilities for The Employer	76

10	Transport, Testing and Commissioning	77

10.1	Transport and Arrival to Site	77

10.2	Mechanical Completion	77

10.3	Punch List	83

10.4	Energisation Tests	84

10.4.1	General Requirements	84

10.4.2	Test Protocol	84

10.4.3	Data to be Provided by Contractor	85

10.4.4	Certification by Contractor of Test Results	85

10.5	Pre-Commissioning Tests	85

10.5.1	Name Plate Capacity Test	85

10.5.2	Functional Tests	85

10.6	Commissioning Tests	88

10.6.1	Transformer Commissioning	89

10.6.2	Scada System Functional Test	90

10.6.3	Security System Functional Test	91

10.6.4	Weather Station	92

10.6.5	Buildings	92

10.6.6	Fire and Smoke Detection Systems	92

10.6.7	High-Voltage Substation Commissioning	92

10.6.8	Commissioning of Components and Systems	93

10.7	Performance Tests	96

10.7.1	Introduction	96

10.7.2	Tests and Acceptance	96

10.7.3	Measurement Requirements	97

11	Form of Progress Reports	99

12	Codes and Standard	101

12.1	Statutory Regulations / Requirements	101

12.2	General Standards	102

12.2.1	Power Transformers	102

12.3	Electrical Equipment	102

12.3.1	Overhead Power Lines	102

12.3.2	General	103

12.3.3	Low Voltage	103

12.3.4	High Voltage	104

12.3.5	Cable Containment, Trenches and Ducting	104

12.3.6	Cable Jointing and Terminations	104

12.4	Security System	104

12.5	Monitoring System	105

12.6	Metering	105

12.7	Mechanical, Civil and Structural Design Standards	105

13	Project Specific Contractor Documents	106

13.1	General Documents	106

13.2	As-Built and Design Documents	106

13.3	Operation and Maintenance Manuals	113

13.4	Other Documents	114

Appendices	116

A.	Employer Provided Documentation List	116

A.1.	Planning Documentation	116

A.2.	Land Lease documentation	116

A.3.	Grid Connection Documentation	116

A.4.	Surveys	116

# Introduction

The following Employer's Requirements are incorporated into the EPC Contract applicable to the construction of the Site Name solar park (Contract).

The site layout is provided in the Project Sharepoint (Site Layout Plan).

## General

These Employer’s Requirements (ERs), contained in Part x of Appendix x of the Contract, describe and make reference to the minimum technical requirements for the Plant, including compliance, scope, design and execution requirements. These ERs must be read in conjunction with the Employer's Requirements document titled "PV Technology Employer's Requirements - Solar PV" contained in Part 2 of Appendix 11 of the Contract (PV Technology Specific ERs) and with the Employer's Requirements document titled "ICP Employer's Requirements - Solar PV" contained in Part 3 of Appendix 11 of the Contract (ICP Technology Specific ERs). The PV Technology Specific ERs and the ICP Technology Specific ERs are together herein referred to as the Technology Specific ERs.

Any approval, document, response, or comment given by the Employer under or in connection with these ERs shall not relieve the Contractor of any responsibility under the Contract, except to the extent expressly provided.

## Definitions

In these ERs, the words and expressions established as definitions in the Contract shall have the same meaning as assigned to them in such Contract. Definitions

In these ERs:

Law (as that expression is defined in the Contract)

Applicable Law means Law (as that expression is defined in the Contract).

CDM Regulations means the Construction (Design & Management) Regulations 2015.

Completion means Provisional Acceptance (as that expression is defined in the Contract)

Connection Agreement means the Grid Connection Agreement (as that expression is defined in the Contract) contained in the Project SharePoint.

Contractor means the Contractor named as such in the Contract

Contractor’s Permits means the Contractor Permits (as that expression is defined in the Contract)).

Contracted Capacity means the maximum export capacity for the Plant as defined in the Connection Agreement.

Defects Liability Period means the Warranty Period (as that expression is defined in the Contract),

DNO (as that expression is defined in the Contract).

Energy Market Operator means National Energy System Operator (NESO)

Environmental Plan means a comprehensive document outlining how the Contractor will ensure it will comply with all environmental requirements of the Contract and/or of the Planning Permission, comprising a part of the Contractor's Construction, Environmental, Waste, Traffic Management Plan as required by the Contract.

Energisation Tests are those tests which shall be performed prior to energisation of the Plant, including pre-commissioning tests, commissioning tests and any tests required by the Connection Agreement.

Energy Meter means any and all import or export meters applicable to the Plant, including any backup or check meters, as defined in the Connection Agreement.

Factory Acceptance Tests means tests to be completed by an original equipment manufacturer at the production facility for the relevant piece of equipment.

Facility or PV Facility means the Plant (as that expression is defined in the Contract).

ICP Contract means any subcontract made or to be made between the Contractor and an ICP Subcontractor in terms as required by the Contract

ICP Contractor means any suitable NERS accredited contractor appointed as subcontractor to the Contractor for the ICP Works

ICP Works means that part of the Contractor's Works as are described and required by the ICP Technology Specific ERs, which may be subcontracted to any ICP Subcontractor under the ICP Contract.

Final Performance Test means the testing set out in Section 10.7, which shall be performed 12 months after the Interim Performance Test.

Good Industry Practice has the meaning given to that expression in the Contract.

Grid Connection Works means the works defined in the Connection Agreement from the DNO.

Health and Safety Plan means a comprehensive document outlining how the Contractor will ensure it will comply with all health and safety requirements of the ERs. The Health and Safety Plan will document, among other things, the Contractor’s health and safety policy, and how it will ensure health and safety risks to its staff, and staff of the Employer, will be maintained at a level as low as reasonably practicable.

Health and Safety File shall have the meaning set out in the CDM Regulations.

Initial Performance Test means the testing referred to in Section 10.7.1 which shall be performed prior to Completion.

Inspection and Test Plan means a document detailing all inspections and tests to be performed by the Contractor, Third Party auditors and the Employer, in order to ensure that the applicable equipment is designed, produced and installed in compliance with requirements of the Contract. The Inspection and Test Plan will include an overview of all tests to be performed throughout execution of the Works, along with detailed test sheets which will be completed during each test or inspection. All test sheets will be provided to the Employer's Construction Asset Manager and/or Technical Adviser once relevant tests are completed.

Interim Performance Test means the testing set out in Section 10.7 which shall be performed 12 months after the Initial Performance Test.

Interconnection Connection Works means the works required to facilitate the grid connection, between the customer’s substation and the Point of Connection (POC).

Irradiance means the incident flux of radiant power per unit area, expressed in units of W/m2 as applied within Section 10.

Levelised Cost of Electricity means the cost of generating a fixed unit of electricity, as defined in Section 1.4.

O&M Contract means the Operation and Maintenance contract for the Plant.

O&M Contractor means a contractor appointed by the Employer to perform operations and maintenance of the Plant after Completion.

Performance Test is defined in Section 10 and applicable PV Technology Specific ERs).

Performance Guarantees means a guarantee offered by an equipment / system supplier to warrant a minimum level of performance of the asset, in relation to Performance Ratio and availability (PV plant) in accordance with the provisions of Section 10 of this ERs and technology specific provisions documents part of this ER package.

Plant has the meaning given to that expression in the Contract.

Point of Connection means the point of Plant connection to the grid network, as defined in the Connection Agreement.

Principal Contractor means the Contractor.

Principal Designer means the Contractor.

Project Management Plan means a comprehensive plan provided by the Contractor that documents how it will deliver its scope of work under the Contract.

Project SharePoint has the meaning given to that expression in the Contract.

PV Monitoring System Availability means the availability of the measured parameters required for the calculation of each Performance Tests. It shall be calculated computing the availability of each measured parameter during all 15-min Test Intervals of the Test Period (Section 10.7).

Quality Plan means a comprehensive document outlining how the Contractor will ensure it will comply with all quality control and assurance requirements of the Contract. The Quality Plan will document, among other things, the Contractor’s quality policy, its plans for audits, contents and timings of submission for the Inspection and Test Plan, how the Contractor will manage records and documentation, including demonstrating traceability of all materials, and how the Contractor will track and address non-conformances.

Recording Interval means time between records.

Regulations means a rule or directive made and maintained by an authority (see ‘CDM Regulations’ and ‘Applicable Law’).

Sampling Interval means time between samples.

Schedule means the Contract Programme (as that expression is defined in the Contract).

Serial Defect has the meaning given to that expression in the Contract

Site Conditions means prevailing meteorological, ground and other conditions experienced at the Site.

Spare Parts has the meaning given to that expression in the Contract

Standards means an established norm or requirement in regard to technical systems specified at the international, national and local level (see ‘Applicable Law’).

Standard Test Conditions (‘STC’) means the reference values of irradiance (1, 000 W/m2), PV cell junction temperature (25 °C) and air mass of (‘AM’) 1.5.

Test means all required technical activities to be performed to demonstrate the Plant and Work has been completed in accordance with the Contract and these ERs. Tests include those specified in Section 10, the Inspection and Test Plan, Quality Plan, the Contract, Technology Specific ERs annexes and any other documentation.

Test Data means data collected during a Test specified in Section 10. The raw data is the data collected prior to applying any quality filter or data treatment to missing or invalid Test Intervals.

Test Data Point Interval or Test Interval means the time between data points recorded in Tests.

Test Period means the time between commencement and finalisation of a Performance Test.

Testing Protocol is defined in Section 10.4.2.

Test Results means the document provided by the Contractor to the Employer for review and acceptance or rejection including, but not limited, the raw data that were collected during the test, data quality check and data filtering and treatment, PR, availability, energy capacity, round trip efficiency, rated power and response time calculations results.

Testing Schedules means Section 10.

Test Modules and Additional Test Modules are defined PV Technology Specific ERs.

Traffic Management Plan means a plan to manage the impact of construction activities on surrounding roads and transportation routes.

Unforeseen Site Conditions has the meaning given to that expression in the Contract

Working Day means Business Day (as that expression is defined in the Contract).

### Abbreviations

Table 1: List of abbreviations

| Abbreviation | Abbreviated Expression |
| --- | --- |
| AC | Alternating Current |
| AMR | Automatic Meter Reading |
| BoM | Bill of Materials |
| BoP | Balance of Plant |
| BoS | Balance of System |
| BSI | British Standards Institution |
| CCTV | Closed Circuit Television |
| CDM | Construction (Design and Management) Regulations 2015 |
| CPP | Construction Phase Plan |
| CT | Current Transformer |
| DC | Direct Current |
| DIN | Deutsches Institut fuer Normung (German Institute for Standardisation). |
| DNO | Distribution Network Oerator |
| EL | Electroluminescence |
| EMS | Energy Management System |
| EN | European Standards |
| EPC | Engineering, Procurement and Construction |
| ERs | Employer’s Requirements |
| FAT | Factory Acceptance Test |
| GHI | Global Horizontal Irradiance |
| GII | Global Inclined Irradiance |
| GPS | Global Positioning System |
| H&S | Health and Safety |
| HSE | Health, Safety and Environment |
| HV | High Voltage |
| HVAC | Heating, Ventilation and Air-Conditioning |
| IBC | International Building Code |
| ICP | Independent Connection Provider |
| IEC | International Electrotechnical Commission |
| IED | Intelligent Electronic Devices such as MV or HV protective relays |
| IEEE | Institute of Electrical and Electronic Engineers. |
| ISO | International Organization for Standardization |
| ITP | Inspection and Test Plan |
| LCOE | Levelised Cost of Electricity |
| LPS | Lightning Protection System |
| LV | Low Voltage |
| MC | Multi Contact |
| MV | Medium Voltage |
| NCSC | National Cyber Security Centre |
| NESO | National Energy System Operator |
| OEM | Original Equipment Manufacturer |
| O&M | Operations and Maintenance |
| PAC | Provisional Acceptance Test |
| PCB | Power Conversion Block |
| PCI | Pre-Construction Information |
| PID | Potential Induced Degradation |
| PLC | Programmable Logic Controller |
| POA | Plane of Array |
| POC | Point of Connection |
| PPA | Power Purchase Agreement |
| PPC | Power Plant Controller |
| PR | Performance Ratio |
| PV | Photovoltaic |
| QA / QC | Quality Assurance / Quality Control |
| SHEQ | Safety, Health, Environment and Quality |
| RfG | Requirements for Generators |
| RTE | Round Trip Efficiency |
| RTU | Remote Terminal Unit |
| RMU | Ring Main Unit |
| SCADA | Supervisory Control and Data Acquisition |
| SLD | Single Line Diagram |
| STC | Standard Test Conditions |
| UBC | Universal Building Code |
| UPS | Uninterruptable Power Supply |
| UTC | Universal Time |
| V | Volt |
| VT | Voltage Transformer |
| MW | Megawatt |
| W | Watt |

## Law, Permits and Standards

The Contractor’s obligation to comply with all relevant Permits and Standards shall include (but shall not be limited to) an obligation to comply with the following:

The requirements of the DNO;

The requirements of Energy Market Operator;

The requirements of the Connection Agreement;

Relevant requirements of the Employer’s Permits (as that expression is defined in the Contract);

All Contractor’s Permits;

Any directive, requirement, instruction, order or guideline issued by a manufacturer of goods, materials and/or plant to be used by or installed into the Plant; and

Any industry norm or best practice.

The Employer has provided a list of Standards applicable to the Work in Section 12.

Within four (4) weeks of signature of the Contract, the Contractor shall produce an exhaustive list of codes and Standards to apply to the design of the Plant for Employer comment. The list of codes and Standards will explicitly justify any deviation from the list of Standards as described in the previous paragraph.

### Technology Specific Requirements

This subsection describes the technology specific Laws, Permits and Standards that are expected to be adhered to, but are not limited to those listed.

#### Interconnection

| Directive 96/92/EC | Rules for the internal market in electricity (EU) |
| --- | --- |
| EU 2016/631 | Requirements for Generators |
| BS EN 61439 (2009 – 2012) | Low-voltage switchgear and control gear assemblies |
| BS6423 (1983) | Code of practice for maintenance of electrical switchgear and control gear for voltages up to and including 1 kV |
| BS 6626 (2010) | Code of practice for maintenance of electrical switchgear and control gear for voltages above 1 kV and up to and including 36 kV |
| BS EN 60422 | Monitoring and maintenance guide for mineral insulating oils in electrical equipment |
| BS 7430 (1998) | Code of practice for earthing |
| BS 7671:2018+A2:2922 IEC 60364 | Requirements for electrical installations. IEE Wiring Regulations. |
| BS EN 50110 Parts 1 and 2 (2004-2010) | Operation of electrical installations |
| BS-EN 50549-1:2019 | Requirements for generating plants to be connected in parallel with distribution networks – Part 1: Connection to a LV distribution network – Generating plants up to and including Type B |  |
| BS-EN50549-2:2019/C1:2019 | Requirements for generating plants to be connected in parallel with distribution networks – Part 2: Connection to a MV distribution network – Generating plants up to and including Type B |
| BS EN 50160 | Voltage characteristics supplied by public distribution networks |  |
| IEC 61727 | Photovoltaic System - Features Interface Connection to the network |  |
| IEC 60616 | Terminal and tapping markings for power transformers |  |

#### PV

PV technology specific standards are listed in different section of “PV Technology specific section”, especially in sections 1.6.4, 1.6.5, 1.14.4 and others for PV specific components, as well as other sections such as 1.6.6 or 1.6.19 for generic components like earthing and cabling.

## General Requirements

The Contractor shall be required to design, procure, construct, commission and test all equipment and perform all services necessary for complete, safe and prudent operation and maintenance of the Plant by others, including information and training, even if not expressly stated in these ERs.

For the avoidance of doubt, it is the Contractor’s responsibility to ensure that the Plant is designed to the latest applicable local and international design criteria and industry best practice.

The Works must satisfy the requirements of the CDM Regulations 2015. The Employer nominates the Contractor as the “Principal Designer” and as “Principal Contractor” for the relevant Works upon award and throughout the pre-construction and construction phase of the Project for the purposes of CDM Regulations and shall be responsible for the implementation of the necessary working practices, procedures and risks assessments.

Documentation provided by the Contractor shall be provided in English.

The Plant shall be located at the Site and shall have a Design Life of 40 years from first export of electricity.

The Plant shall be designed, manufactured, configured and constructed in such a way that it shall achieve performance, availability and reliability in line with the Contract requirements. The designs, components and Materials to be used by the Contractor shall be of proven quality and track record, having been satisfactorily used in recent project financed, utility scale, international PV and other Renewable projects.

The Plant shall be designed in such a way that the maximum power output (active power) measured at the Point of Connection (POC) is consistent with requirements of the Connection Agreement and PPA (if any).

The Contractor shall optimise the Plant’s LCOE considering the design, operation and maintenance requirements for the Plant. The LCOE is calculated factoring in all costs associated with engineering, procurement, construction, operation, maintenance, decommissioning and rehabilitation of the Plant and Site, using methodology and assumptions considered appropriate by the Employer.

The LCOE will be calculated as.

LCOE = discounted capital costs + discounted operational costs + discounted decommissioning costsdiscounted generation

Commissioning and Completion testing of the Plant shall be undertaken by the Contractor, in coordination with any ICP Contractor. The tests will ensure that the Plant can operate and perform in accordance with these ERs and the Contract. Testing will be undertaken to verify the performance of the Plant, and successfully passing all tests will be a condition for achieving Completion.

# General Scope of the Works

The Contractor’s overarching scope of Work is detailed in this Section 2. The Project specific scope of Work is detailed in Technology Specific ERs.

## Preparatory Works

The Contractor shall be responsible for providing preparatory works, including but not limited to:

Site preparation, including clearing and grubbing of land, conservation of topsoil, excavation, backfilling, compaction, grading, levelling, earth moving, soil improvement, and rehabilitation of parts of the Site as affected by the Contractor’s activities;

Sourcing of external fill and grading material with proper origin certification;

Pre-commencement site survey detailing the status of the Site before any works for full reinstatement after (i) construction; (ii) de-commissioning; (iii) compliance with terms of lease/land agreements;

Site drainage and sewage systems;

All necessary Site control measures during and after construction (i.e., erosion, flooding, and dust control);

Preparation of stable foundations, in compliance with equipment manufacturers’ requirements and specifications; and

Liaison with and accommodation of the interests third parties may have regarding the Site, the Plant or access or proximity thereto.

## Infrastructure Works

The Contractor shall be responsible for providing infrastructure works, including:

Construction, maintenance and reinstatement of access roads and roads within the Site;

Water and electricity supply required for construction;

Internet and Wi-Fi connection with a minimum bandwidth of 10 Mega-bits per second, including providing unrestricted access to the Employer;

Construction of all necessary sewage infrastructure to serve the Plant;

Construction of electrical distribution system, water system, parking areas, etc;

Fencing, gates and intruder alarm systems appropriate for the Site Conditions, in order to ensure safety and security of the Plant, equipment and personnel;

Sourcing of water, energy, heat, compressed air and any other utility or form of energy needed during construction;

Firefighting and first aid infrastructure;

Spill kits to address any spillage control requirements for the Materials on site;

Removal of temporary works after construction;

Relocation of any cables and pipes (i.e. existing services and/or infrastructure) crossing the Site (if any), including any replacement materials required as a consequence of the relocation;

Reinstatement of vegetation as per local environmental requirements; and

The Contractor is responsible for damage due to construction activities caused to private and public infrastructure inside and outside of the Site, and the restitution thereof, to the requirements and satisfaction of the relevant Employer’s, users and authorities.

## Construction Facilities

The Contractor shall be responsible for providing construction facilities, including:

Provision of a suitable part of the Site for the location of the Contractor’s facilities (including toilets, corresponding sewage treatment, catering), security control (access control, security patrolling, etc.) and temporary storage. The location of the facilities shall be agreed with the Employer, areas reserved as indicated on the Site Layout Plan . If an off-site temporary construction compound is envisaged this shall only be permitted with the prior consent of the Employer and the Contractor shall be responsible for obtaining land lease, permits and any costs associated with the off-site compound;

Provision of temporary Contractor's offices, warehouses, workshops for construction, along with all vehicles, plant, mobile equipment, temporary power generators, temporary air compressors;

Provision of temporary Employer’s and Employer’s engineer offices and associated services (ablutions, electricity, HVAC, etc.) as further detailed in Section 9.13; and

Removal of temporary construction facilities including complete rehabilitation of surface areas disturbed during construction.

## Design and Engineering

The Contractor shall be responsible for all engineering and design activities related to the Plant, including the related Interconnection Connection Works, which form part of the Plant as further detailed in Section 10.

The detailed design and engineering shall achieve:

Full compliance to the relevant Grid Code and suitable to connection to the GB transmission system;

An optimised LCOE;

Optimised operation and maintenance of the Plant;

Export capacity, measured at the Point of Connection, to not exceed the Contracted Capacity;

Import capacity, measured at the Point of Connection, to not exceed the Contracted Capacity

Spare capacity, measured at the end of construction, to have at least 15% system margin (thermal and fault level) and spare space for at least 15% more equipment;

Avoid single point failures and have adequate redundancy;

Maximise performance and availability

The PV Facility shall be designed such that availability shall meet or exceed 99% over its design life;

A design which can be manufactured, installed, operated and decommissioned safely over its lifetime. The Contractor shall propose and perform all studies necessary to achieve such a design, including any necessary hazard identification studies. The design shall also facilitate ease of operations and maintenance and due consideration given to adequate access for repair and replacement.

## Procurement and Delivery

The Contractor shall procure, be responsible for and take care of, at its cost, the procurement, manufacturing, loading, unloading, transportation and logistics of all material, equipment and tools necessary for the execution of the Plant, including customs clearance and associated costs and, maintaining the original equipment manufacturer’s warranty and obtaining and maintaining appropriate insurance.

In selecting components to be incorporated and integrated into the Plant, the Contractor shall evaluate the production quality, performance, OEM’s UK service and spare parts availability, efficiency, and reliability of current technologies available, including the determination and mitigation of deficiencies and limitations of each component and/or technology with respect to Site Conditions, in order to achieve an optimised design, installation and performance.

The Contractor shall be responsible for care and custody of the Site, the Work, Materials and the Plant until Completion.

As part of its Quality Plan, the Contractor shall maintain a system to monitor delivery, storage and installation of Materials. For the avoidance of doubt, the Contractor will be responsible in case of damage to the Materials, including any Free Issued Equipment which has been issued to the Contractor.

## Transportation and Logistics

The Contractor shall be responsible for selecting in compliance with the Employer's Permits all transport routes and arranging all necessary transport and logistics for its scope of Works. The Contractor shall bear responsibility and assume all costs associated with:

Any road or access modification or reinforcement required to transport the equipment to the Site from the place of origin;

Any permit, license and approval required to transport the equipment to the Site from the place of origin;

Any temporary storage facilities required during the transportation and logistics phase;

Implementing GPS tracking for logistics vehicles; and

All logistics vehicles will be subject to a 5-year vehicle age limit.

As part of its Environmental Plan, the Contractor must prepare a Traffic Management Plan that complies with all relevant conditions of the Employer’s Permits and Contractor’s Permits. The Traffic Management Plan shall be subject to Employer comment. Where relevant, the Traffic Management Plan will outline where sections of the route need to be modified to meet delivery requirements for Equipment or Materials. The Contractor shall be responsible for completing any road modifications required in order to comply with the Traffic Management Plan. Roads must be re-stated to their original conditions prior to Completion unless agreed otherwise with the Employer and other relevant stakeholders.

Outline Traffic Management Plans and Site Access Maps have been included within the available supporting documentation for this Plant.

The Contractor must prepare a journey management plan that will outline the route, expected journey time and associated rest stops which hauliers will be required to adhere to. Travel times and associated rest periods will comply with local transport and logistics regulations.

Shock sensors shall be applied to sensitive equipment, such as module pallets, switchgear etc., prior to transport to detect shock loading above and beyond an acceptable level. A full visual inspection of all Equipment arriving at Site shall be performed including checking shock sensors on sensitive equipment.

## Surveys, Studies and Reports

The Contractor shall, as a minimum, prepare and complete the following surveys, studies and reports and undertake a detailed design for the Plant, suitable for the Site, including:

Compliance with relevant UK standards, approvals and statutory requirements.

Identification and assessment of all utilities within the vicinity and surrounding the site for development.

Topographic contour data collection and site mapping/surveying.

Surveys to evaluate shading objects including visible young trees or potential future construction affecting energy production.

All geotechnical, geophysical and seismic investigations (if required to supplement the Employer’s geotechnical survey).

Soil electrical and thermal resistivity testing.

Moisture content and sieve tests of cable bedding materials (on and off-site).

Additional geotechnical and materials testing including CBR tests, plate bearing tests, and boreholes in relevant locations.

Flood and drainage studies.

Hydrology studies including the required volume of water to construct, operate and maintain the plant and how this water will be sourced.

Design of surface water drainage systems including swales, ditches, filter drains, attenuation tanks, soakaways and outfalls.

Flood mitigation works including exceedance routing, flood compensation areas and protection bunds.

Solar resource analysis, performance ratio studies and energy yield assessments.

Meteorology studies including lightning study.

Wind studies and associated load assessments including static, dynamic and fatigue loading.

Grid connection studies and grid code compliance analysis.

All necessary calculations for civil, mechanical and electrical systems including structural and foundation loading calculations, drainage calculations, power loss calculations, voltage drop calculations, load flow studies, protection coordination, fault level calculations, cable sizing calculations, fuse and switchgear sizing, earthing, bonding and lightning protection, and insulation coordination.

Preparation of all required drawings including schematic drawings, building and station layouts, component specifications, bulk material specifications, arrangement and layout drawings, mounting structure and reinforcement drawings, trenching drawings, steel structure drawings, single line diagrams and typical construction drawings.

Preparation of design, concept and philosophy documents relating to control systems, monitoring systems, plant management systems and SCADA compatibility.

Preparation of all design documentation including construction drawings, maintenance manuals, start-up procedures, commissioning procedures and handover procedures.

Submission of statutory and design code calculations for third-party verification.

Obtaining all required approvals and certifications.

The Employer’s development studies have been made available to provide an indication of the Site Conditions. These documents can be found in the Project SharePoint.

## Equipment and Systems

As a minimum the following equipment and systems are to be supplied by the Contractor as part of the Work:

Grid compliance equipment

Step-up transformers;

Cables (DC, AC, communication, fibre-optic, etc.) ;

Containers and cabinets;

Interconnection Works;

Heating, ventilation and air conditioning (‘HVAC’) system as required;

Fire protection systems;

Fire-fighting system;

Electrical protection systems;

Lightning protection system (‘LPS’);

Earthing and bonding system;

Weather stations;

Supervisory, control and data acquisition (‘SCADA’) system;

Metering systems;

Security and surveillance systems;

Access control systems;

Drainage systems;

All consumables for construction and operation of the system until Completion;

General site facilities;

Waste-water system;

Signs and safety equipment;

SHEQ equipment and tools;

A set of Spare Parts and

Any other equipment or component that, although not listed here, is necessary for the construction, connection to the grid and proper, safe and efficient operation of the Plant with due consideration of the Plant’s Design Life.

The Contractor is responsible for providing all consumables it requires to construct the Plant in accordance with the Contract, to achieve Completion.

## Construction

The Contractor shall be responsible for completing all construction works as necessary, including but not limited to those items listed within this Section.

### Civil Works

Setting-out works and pre-construction surveys

Site clearance and preparation, including clearing, mowing, excavation and disposal of materials

Geotechnical and materials testing (additional CBR, plate bearing).

Temporary services and welfare facilities

Dewatering and groundwater control measures

Tree and Hedgerow protection in accordance with the BS Standards

Silt Fencing and watercourse protection in accordance with the BS Standards

Ground improvement and soil bearing capacity enhancement as required (e.g. soil stabilisation, piling, stone columns)

Excavation, backfilling and compaction works

Foundations and support structures, including concrete and reinforced concrete works for plant, equipment, buildings, fencing, CCTV and lighting

Crane pads, hardstandings, heavy-duty loading areas, and other temporary works as required

Cable trenching, duct systems, cable trays, duct protection, and concrete encasement where required

Construction of buildings, including administrative buildings, control rooms, workshops, storage buildings, guard houses, auxiliary buildings, and buildings for mechanical and electrical equipment (including substation and interconnection works)

Roads, external highway tie-ins, and access works where required

Plant and site drainage, surface and road drainage, and wider water management measures

Water supply infrastructure to the site (e.g. rainwater harvesting, private water supply, and water main connections)

Fencing, access control, and security systems

Landscaping, ecological mitigation, site reinstatement, and rehabilitation during and after construction

As-built surveys and preparation of record drawings

### Mechanical Works

Structures for inverters, isolators, meteo panels, outstations, and all relevant structures for ancillary equipment

Generating equipment installation;

Balance of mechanical equipment;

Auxiliary systems, as far as applicable;

HVAC to all buildings as applicable;

Equipment for workshop, stores and other facilities, including storage racking;

Erection of transmission line pylons;

Cable trays;

Structures for weather stations;

Fire detection and fire protection devices and equipment; and

Emergency power facilities where required.

### Electrical Works

Electrical cabling for ancillary and auxiliary devices

Grid Compliance Components

Electrical string cables between modules;

Electrical cabling between combiner boxes (if applicable) and inverters;

Electrical cabling between PV Inverters, AC Isolators and Transformers;

HV Electrical cabling until Point of Connection;

HV switchgear and LV/HV transformers;

SCADA compatible equipment;

SCADA system (itself, installed and governed by the Contractor with power supplies to be supplied by PV and ICP Contractors as per locality);

Electrical equipment within the Facility and Plant substations;

Control cabling;

Meters, as specified in the Plant’s Connection Agreement;

Lightning protection system and system earthing;

Installation of transmission line cabling;

Installation of cabling to substations;

Grid Connection Works;

All required electrical protection;

Electrical system related to security such as CCTV (itself, installed and governed by the Contractor with power supplies to be supplied by PV and ICP Contractors as per locality) and access control;

Auxiliary power supply and connection; and

Weather station.

## Parts and Tools

The Contractor shall provide at its own cost all consumables, goods, Materials and Spare Parts necessary for discharging its responsibilities under the Contract, including commissioning, and during the Defects Liability Period.

The Contractor shall have an ongoing obligation to implement a system to track consumables, goods, materials and Spare Parts (itemised) that have been ordered, shipped to, delivered to, installed and commissioned at the Site. The Employer shall have the right at any time to undertake audits and verification of the Contractor’s Materials tracking system. The Contractor’s tracking system shall comprehensively provide the list of, where relevant, the following:

A unique identification number (manufacturer’s serial or stock number);

Item description;

The part of the Facility the item is associated with;

Recommended quantities;

Cost per item;

Country of origin / supply;

Identity of manufacturer;

Identity of supplier;

Anticipated procurement lead-times;

Special / abnormal procurement (to the Site) requirements (if any);

Storage requirements; and

Confirmation that the item and the handling and storage at Site thereof complies with warranty / guarantee requirements.

All tools, equipment and plant to facilitate maintenance of the Plant (including if required, module cleaning equipment) shall be provided by the Contractor and shall be included in the Contract Price. Tools are regarded as any proprietary, non-consumable equipment required for the efficient and safe operation and maintenance of the Facility. For the avoidance of doubt the tools shall be warranted and repaired or replaced for the duration of the Defects Liability Period.

The Contractor shall provide a comprehensive list of tools, equipment and plant, indicating the following:

A unique identification number (manufacturers serial or stock number);

Tool description;

Where the tool is to be utilised i.e. the specific component or equipment within the Plant;

Quantities;

Cost per item;

Country of origin / supply;

Identity of manufacturer;

Identity of supplier;

Anticipated procurement (to the Site) lead-times;

Replacement intervals; and

Calibration requirements.

Any specialist tools necessary to perform maintenance of the Plant will be supplied by the Contractor prior to commencement of commissioning. The Contractor shall identify which tools shall be provided to the Plant.

## Software

The Contractor shall design the Plant and prepare any study or evaluation using software tools and programs consistent with good industry practice.

The Contractor shall provide all software and required software licences required for the efficient and safe operation of the Facility, together with a list identifying:

The identity of the licensor;

The name of the software;

The systems or equipment the software is associated with;

The software update version number;

The method of software update; and

Confirmation that the Contractor has arranged for the currency of the software (and support) for the duration of 30 years as from Completion, including all subsequent updates.

All software installed on the Facility’s equipment shall be licensed, for the current version as at the date of Completion, excluding updates, and shall be valid for a minimum of 40 years from the date of Completion. License fees that authorise updates and support for the installed software shall be timeously paid by the Contractor until the end of the Defects Liability Period.

## Performances, Tests and Warranties

The results of any Performance Test shall be the values recorded and calculated. Testing uncertainty shall be a measure of the quality of the test and shall not be a tolerance or additional allowance on the pass/ fail criteria.

The Contractor shall undertake, at its responsibility and cost, all factory, pre-commissioning and commissioning tests as detailed in Section 10 and any other tests necessary to demonstrate the quality and reliability of the Facility.

In addition, the Contractor shall provide warranties and guarantees for the main equipment and components of the Facility with minimum durations as specified in the Contract

Other than those specific testing requirements to be completed by others as documented in the Connection Agreement, the Contractor shall carry full responsibility for the testing of the Facility to the full satisfaction of the Connection Agreement and local Grid Code.

The Contractor shall coordinate with any ICP Subcontractor the performance tests that are required to be performed by each of those parties to the technology specific Facilities under their responsibility, as indicated in the respective Technology Specific ERs.

The Contractor shall, in consultation with the Energy Market Operator, propose a full test programme in order to demonstrate compliance with the National Grid and Energy Market Operator requirements, in order to achieve Completion on or before the Guaranteed Completion Date.

The Contractor or any ICP Subcontractor shall provide a provisional testing programme for Grid Connection Works within 90 Days of Notice to Proceed, and shall co-ordinate with the Contractor, Energy Market Operator and Employer to ensure a final test programme is agreed at least 90 Days prior to the Plant’s energisation date.

## Documents

The Contractor shall prepare all required documentation and manuals whilst ensuring that they conform to relevant Standards.

The Contractor shall make available in due time such documentation to the Employer in electronic and paper form.

All documentation should be available in English, any drawings in .dwg and PDF, any living documents should be available in their Microsoft Suite format (e.g. .docx, .xlsx) and PDF.

## Training

The Contractor shall plan, manage, and conduct a training programme for the Employer’s personnel and O&M Contractor. All training activities and materials shall be competently conducted in English.

The Contractor shall conduct a single training programme for up to fifteen (15) personnel designated by the Employer and additional personnel as designated by the O&M Contractor. The training shall be conducted over a minimum of five (5) days and in line with any terms prescribed in the Contract. The training session shall be completed at a date to be agreed with the Employer, and at the latest prior to Completion.

Training topics shall include:

Site personnel safety;

Emergency inverter and plant shut down procedure;

Inverter start up procedure;

HV infrastructure operations and maintenance;

Any requirements of the DNO e.g. inter-trip schemes and how these have been accommodated in the design;

O&M manual detailed review;

Future replacement of major parts strategy, including maps of indicative plant (i.e. crane) placement;

Facility operations and procedures;

Review Site maintenance plan;

Detailed review of as-built drawings;

Cleaning/washing process of module surface (in case of unexpected dirt) including any particular requirements for the specific module type and installation configuration. [PV only]

Deactivation and re-activation of all alarm systems;

Remote access to cameras and the audio warning system;

Use of all keys and/or access control systems;

Failure detection and prevention;

Walking tour of security system;

Simulated release of alarm and action required; and

SCADA system demonstration including alarm/fault code identification and resetting and compilation and export of data.

The Contractor shall gather from the suppliers (PV modules supplier, substation equipment supplier, etc.) any information related with a safe operation and maintenance of the supplied equipment (e.g. safe installation and connection of PV modules, electrical hazard, fire hazard, etc.). The Contractor will integrate in its training programme all the topics covering the safe operation of the equipment and Facilities that are part of the overall Plant.

A detailed training programme shall be provided by the Contractor to the Employer 45 Days prior to the start of the training course. The training program shall be subject to Employer comment. Final training manuals shall be made available to participants no later than 10 Business Days in advance of the agreed commencement of the training.

## Compliance

### Permit Compliance

The Contractor shall obtain the Contractor’s Permits and maintain the Contractor’s Permits in full force and effect for the duration necessary to perform its obligations under the Contract. The Contractor is also responsible for ensuring that the Works are undertaken within the terms relating to the design and/or construction of the Works within the Permits and any relevant planning permissions executed by the Employer.

### Connection Agreement

The Contractor is responsible for ensuring that the Works are undertaken in compliance with all terms set out in the Connection Agreement

The ICP Works will be undertaken by the Contractor but may be subcontracted to an ICP Subcontractor. The Contractor must make sure that all equipment installed is compliant with the Grid Offer and any DNO and National Grid regulations and standards and compatible with any ICP Subcontractor’s equipment. More details on each Contractor’s responsibilities are included in the Responsibility Matrix.

### Lease Agreements

The Contractor is responsible for ensuring that the Works are undertaken within the terms relating to the design and/or construction of the Works within the Land Leases and any relevant Easements executed by the Employer, excluding any obligations relating to payment.

The Land Lease and Easements documents are included in the Project SharePoint

## Quality, Health, Safety and Environment

The Contractor will be required to:

Implement and maintain a health and safety system compliant with OSHAS 18001 / ISO 45001 – Occupational health and safety, good industry practice, and all applicable Law and regulations;

Implement and maintain a quality management system compliant with ISO 9001 and good industry practice;

Implement and maintain an environmental management system compliant with ISO 14001 — Environmental management system, good industry practice, and all Applicable Law and Regulations;

Submit to the Principal Designer; and

And if requested Act as “Principal Contractor” upon award and throughout the pre-construction and construction phase of the Project for the purposes of the Construction (Design and Management) Regulations 2015 (the “CDM Regulations”) and shall be responsible for the implementation of the necessary working practices, procedures, and risks assessments.

The Works must satisfy the requirements of the CDM Regulations. Please see section 2.16.1 for further information on CDM regulations.

Within four weeks of Notice to Proceed, the Contractor will produce a project specific Health and Safety Plan, Quality Plan and Environmental Plan which demonstrate how the Contractor will ensure compliance with requirements of the Contract. The Health and Safety Plan, Quality Plan and Environmental Plan will be subject to Employer comment and will be strictly adhered to by the Contractor in performing the Work.

The Health and Safety Plan shall include, but not be limited to:

An Emergency Response Plan which shall be produced in consultation with the Employer and all relevant stakeholders (including ICP Contractor);

Training matrix for all Contractor staff;

Schedule for completion of drills (fire, security, etc.);

Schedule for delivery of awareness campaigns; and

All other topics to be covered by a qualified contractor acting in line with good industry practice.

The Employer reserves the right to audit any and all aspects of Contractor’s health and safety system, quality management system and environmental management system to confirm work is being performed according to the Health and Safety Plan, Quality Plan and Environmental Plan. The Employer’s audit rights will include attendance at Subcontractor and supplier facilities, either for isolated visits prior to or during production, or with a part-time or full-time presence. The Contractor shall ensure all documentation necessary to confirm the Contractor is in full compliance with requirements of the Contract is made available to the Employer and its representatives.

### Construction, Design and Management (CDM) Regulations 2015

The Employer, Designers, Principal Contractor, other contractors and the Principal Designer all have legal duties in respect of the CDM Regulations.

The role of Principal Designer will be allocated by the Employer. The CDM boundary shall be the whole of the Project Works / Site.

The Contractor shall review all design requirements in these Employer’s Requirements and take into consideration any risks associated with the safety of persons during the construction and operation of the Project.

The Contractor shall meet and comply with the requirements for CDM and environmental management and performance throughout the duration of the Contract including project development, design work, risk assessment, construction and commissioning.

The Contractor shall appoint a Health, Safety and Environment (HSE) manager responsible for ensuring that the Works are carried out in accordance with the CDM regulations and national health and safety requirements, industry best practises, Applicable Laws, Regulations, and statutory requirements.

The Contractor, in its role as Principal Contractor, shall provide maintain and keep up to date all necessary H&S documentation during the planning, design and construction of the Works in line with an agreed HSE management plan, as required under the CDM Regulations.

A formal Pre-Construction Information (PCI) report, as detailed in the CDM Regulations, shall be agreed with the Contractor to confirm project-specific H&S information in order to identify any pertinent hazards and risks associated with the Works. This shall be uploaded to the Project SharePoint once complete, and the Contractor shall comply with its requirements and shall cause all of its subcontractors to comply with its requirements.

The PCI, and any other relevant information, shall provide the basis for the Contractor preparing the Construction Phase Plan (CPP) as required under the CDM Regulations. The CPP is to be completed and submitted to the Employer and Principal Designer for approval prior to construction works starting.

Towards the end of the Works, the Contractor, in its role as Principal Contractor, shall provide the Employer with all necessary documentation deemed necessary for inclusion in the Health and Safety File, as required by the CDM Regulations.

If more than one contractor is used by the Contractor to design the Works, the Contractor shall fulfil a thorough check of all documentation. The Contractor will be responsible for planning, managing, monitoring and co-ordinating H&S in the pre-construction phase, and making sure that any risks which need to be controlled during construction are well understood. The Contractor as Principal Designer shall review the H&S documentation provided by its Subcontractors to ensure that they eliminate hazards and control risks associated with the Works. This obligation extends to all subcontractor works associated with or included in this Contract. The Contractor as Principal Designer shall provide all necessary support and assistance to ensure that the Employer is in compliance with and fulfils its duties under the CDM Regulations.

Throughout the Works, the Contractor as Principal Designer, on behalf of the Employer, shall prepare and keep up to date the Health and Safety File for the project. The Health and Safety File shall contain all information needed for future construction and operations work, including cleaning, maintenance, alterations refurbishment and demolition to be carried out safely, as required by the CDM Regulations.

The Contractor as Principal Designer shall ensure that all necessary documentation required from itself as the Principal Contractor, other contractors, sub-contractors and designers are requested and included in the Health and Safety File in a timely fashion.

## Internal Connection Works

The Contractor shall be responsible for the design, installation and testing of the Works required to achieve internal connection of the Plant in accordance with the requirements of the Connection Agreement, ICP Works requirements and all Applicable Laws and Permits.

The Employer shall act as the counterparty to the Connection Agreement. For the avoidance of doubt, the Contractor shall provide all assistance reasonably requested by the Employer, as may be necessary to ensure that that connection occurs in line with the Schedule and requirements of the Connection Agreement.

The Contractor shall provide all reactive power compensation equipment or harmonic filters specified in the Plant’s Connection Agreement as part of the Contract Price.

## Substation and O&M Building

The Contractor is responsible for the design, procurement, and construction of the on-site substations and for the provision of all furniture and equipment required. The Contractor shall provide the Employer with proposed furniture specifications and layout plans prior to installation for Employer’s approval.

The Contractor must provide all the necessary heating, ventilation and air conditioning (HVAC), electrical power, lighting, communications, internet and security, fire detection, emergency exits and hydrants, drainage, trenching, structural, adequate potable cold and hot water, and sewerage services for the substation building, as required by that building's function. These must be designed to be appropriate for the specific Site Conditions including consideration of climate and geotechnical conditions. For the avoidance of doubt, the Contractor’s scope of work includes all correspondence with authorities and commercial entities associated with provision of utilities, and sourcing permits and appropriate commercial agreements to ensure all utilities are available to the Plant for its Design Life.

The substation building shall contain the following rooms:

Facility HV switchgear and HV transformer room(s);

Control/SCADA room;

Storeroom for spare parts;

Control and Meter room;

Auxiliary Transformer room

1 x office for three people; and

1 x space for a portable toilet.

Switchgear and transformer room will be appropriately sized consistent with all Applicable Laws, Standards. Rooms will be provided with appropriate climate control to ensure switchgear and transformers remain within specification.

The control/SCADA room shall be appropriately sized for all SCADA equipment. Adequate HVAC shall be provided to this room to ensure a temperature range within the room at all times to meet requirements of the SCADA system design.

The meter room shall be appropriately sized for the meters specified in the Connection Agreement and LV meter if separate LV feed will be obtained.

The Contractor shall implement access control arrangements for all relevant enclosures. including the switchgear and transformer room, control/SCADA room, meter room and storeroom so enclosures can only be accessed by the authorised and suitably qualified on-site and O&M personnel.

## Operation and Maintenance Building

The Contractor shall provide an O&M building which can be utilised by the Employer, their personnel and the operation and maintenance contractor during the operation of the Plant.

Building shall contain the following:

Control and operations room;

Offices;

Kitchen/lunchroom:

Including sink and area for food and drink preparation;

Toilets:

Separate male and female toilet;

All required services including but not limited to;

Pad lockable latch on all doors, including vandal proof cover over latch;

Security bars and fly mesh across windows;

Rubbish bins;

Supply of potable water, this may be from the inclusion of storm-water storage facilities and / or connection to the local water supply;

The potable water design must allow for all aspects of water quantities including any requirement for fire control and pressurisation; and

A potable and non-potable water system for twenty full time staff on site.

The Contractor shall provide all waterproofing, insulation, finishes, furniture, fixtures, fittings and equipment for the O&M building to a high standard of quality and subject to the Employer’s approval.

The Contractor must provide all the necessary civil and structural works, mechanical, electrical (power, UPS, earthing, emergency and normal lighting, communications, internet and security), fire (detection and suppression), civil (drainage, trenching, structural) and hydraulic (potable cold and hot water, recycled grey water supplies and sewerage) services, first aid station and eye wash (if applicable), desks and chairs and outdoor car parking for the O&M building, as required by that building's function.

These must be designed to be appropriate for the specific Site Conditions including consideration of climate and geotechnical conditions. The O&M building must be designed to withstand all expected loads of occupation and operation for the specified Design Life. The Contractor will provide for all aspects of this system including the route, trenching and connection details.

Control / Operations Room

The Contractor must provide a Plant control / operations room. This room must house the following:

Workstations and HMI, including visualization of the monitored equipment, for two staff including telephones;

Security system displays (minimum 19-inch monitor); and

Air-conditioning suitable for the number of occupants;

Spares Cabin

The Contractor must provide a separate spares cabin to store all Plant related spare parts, which is maintained at the temperature and humidity range specified by the manufacturers of all the components stored in it (including transformers where requested) to maintain the manufacturer warranties of the Spare Parts. This shall have a lockable enclosed storage area for the storage of Spares, Consumables, components and a working area for maintenance activities. The storeroom shall be sized to accommodate the full set of Spare Parts. The stores shall also retain spares to carry out recommended routine and scheduled servicing of the Plant. As a minimum the lockable storage area needs to be large enough to accommodate the Spares required for the O&M of the Facility plus 40% more space.

This building shall have a concrete base sufficient for the loads to be expected. It shall be provided with lighting and power for all areas.

Access to the Warehouse shall be via pedestrian door and at least two double doors sufficiently wide enough for the easy egress of all vehicles and Spares.

## Earthing System

The Contractor shall provide the complete earthing system, based on the Earthing Study, to provide a safe Plant. The earthing design must comply with the Grid Code and Applicable Standards and be verified and approved by the Contractor or any ICP Subcontractor for integration compatibility with the Plant’s earthing system.

There will be a single earthing grid for the whole Solar PV. The earthing grid will consist of bare copper cable or tape (buried horizontal electrode);

There will be a single earthing grid for the whole gird connection compound. The earthing grid will consist of bare copper cable or tape (buried horizontal electrode); and

Each of the systems will be interconnected to provide an entire Plant-wide earthing system, governed (designed, implemented and tested) by the Contractor or any ICP Subcontractor.

The relevant fundamental earthing design parameters such as fault current and fault duration shall be agreed between Contractor and any ICP Subcontractor. The earthing system shall maintain step, touch and transferred potentials within the voltage limits recommended according to Applicable Standards. The Contractor will determine the method of neutral earthing for the HV and the LV system and resulting ground fault currents as per Applicable Standards and Grid/Distribution Code requirements:

Ungrounded neutral system;

Solid neutral earthing system;

Resistance neutral earthing system;

Resonant neutral earthing system; and

Transformer or neutral electromagnetic coupler (NEC) earthing system.

The transformers’ neutral points will be connected to the earthing grid, if applicable.

The Contractor shall perform appropriate calculations and field tests before energizing the Plant.  The Contractor shall add additional earthing conductors (if required) inside the main earthing loop of the Plant in order to ensure that neither step nor touch voltage can reach dangerous values in any point of the Plant under the agreed fault conditions.

Adequate earthing must be maintained throughout all metal work across the Plant through adequate bonding connections to the main earthing grid. All electrical systems and exposed metal work must be considered within the design of the earthing system and connected where required.

The Works shall provide for a fully protected robust earthing system for lightning protection. The design shall adhere to the Applicable Standards appropriate for the Plant, as verified and approved by the Contractor or any ICP Subcontractor.

Further requirements for the Plant’s earthing system are indicated in section 9.7.

## Lightning System and Overvoltage Protection

A lightning and overvoltage protection system shall be designed according to Applicable Standards and the Insulation Co-ordination Study (to be conducted by the Contractor or any ICP Subcontractor).

The PV System shall be equipped with a Lightning Protection System (‘LPS’), whose LPS class should be consistent with the lightning risk assessment. The risk assessment should be undertaken to define the protection against physical damage to structures, life hazard and protection of electrical and electronic systems, according to Applicable Standards.

The main components and systems belonging to the PV System’ lightning protection system are listed below:

External lightning system (structural lightning protection); and

Internal lightning protection (electrical and electronic system protection).

Further requirements for the Plant’s lightening and overvoltage protection are indicated in section 9.7.

## Employer Provided Equipment

[Not Used]

## System Design and Installation Standards

### General

[NESC (ANSI C2), National Electrical Safety Code for Electric Supply Stations and Equipment;

IEC 60950-1:2005, Information technology equipment- Safety –Part 1: General requirements;

IEC 60364 (all parts), Low-Voltage electrical installations (for topics not included in the National Electrical Standards and National Electrical Safety Code);

IEC 62262:2002, Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts (IK Code);

IEC 61936-1:2010+AMD1:2014 Power installations exceeding 1 kV AC;

IEC 60529 (all parts), Degrees of protection provided by enclosures (IP Code);

IEC 60071:2018 SER, Insulation co-ordination - ALL PARTS;

IEC 61850: 2018 SER, Communication networks and systems for power utility automation –ALL PARTS; and

National Fire Prevention regulations.

### Earthing Standards

IEEE Std. 80-2000, IEEE Guide for Safety in AC Substation Grounding;

IEEE 142-2007 IEEE Recommended Practice for Grounding of Industrial and Commercial Power System;

IEC 61936-1:2010+AMD1:2014, Power installations exceeding 1 kV AC. – Part 1: Common rules;

IEC 60364-7-712, Solar photovoltaic (PV) power supply systems;

IEC 60999 (all parts), Connecting devices. Electrical copper conductors. Safety requirements for screw-type and screwless-type clamping units;

IEC 60071-1:2006, Insulation co-ordination - Part 1: Definitions, principles and rules ;

IEC 60664-1:2007, Insulation coordination for equipment within low-voltage systems - Part 1: Principles, requirements and tests;

IEC 61557-8: 2014, Electrical safety in low voltage distribution systems up to 1000V AC and 1500V DC - Equipment for testing, measuring or monitoring of protective measures - Part 8: Insulation monitoring devices for IT systems;

UL 1053 Standard for Ground-Fault Sensing and Relaying Equipment; and

IEEE 81-2012- IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potential of a Grounding System.

### Overvoltage and Lightning Protection

IEC 62305:2013 SER, Protection against lightning - ALL PARTS;

IEC 60099-4: 2014, Surge arresters – Part 4: Metal-oxide surge arrestors without gaps for AC systems;

IEC 60099-5:2018, Surge arresters – Part 5: Selection and application recommendations;

IEC 61643-11:2011, Low-voltage surge protective devices - Part 11: Surge protective devices connected to low-voltage power systems - Requirements and test method;

IEC 62561 (all parts), Lightning Protection System Components (LPSC); and

IEC/TS 60479-1:2005 Effects of current on human beings and livestock - Part 1: General aspects.

## Inspection and Testing of Major Components

The Contractor shall be responsible for conducting all tests in such a way as to protect the safety of all persons and the Works and in accordance with relevant Law. The Contractor shall provide an appropriate training for all personnel on the Site who will be involved in or witnessing any Tests, and shall ensure that such personnel comply with all applicable safety procedures at all times during performance of the Tests. The Contractor shall discontinue performance of any Tests in the event of any unsafe conditions.

The Contractor is responsible for all equipment, materials and labour required for testing. In the event of failed Tests the Contractor is responsible for rectification and re-testing until the Test is passed. The Contractor shall provide all reports, calibration/test certificates and documentary evidence required by the Employer to verify all Tests have been passed.

### Factory Inspection and Testing

Upon finalisation of preferred equipment suppliers, the Contractor shall advise the Employer as to the location of manufacture of each of the key equipment items including (modules, mounting structures, inverters, isolators, transformers, HV switchgear, meters, pre-fabricated buildings and others as reasonably requested by the Employer).

The factory inspection aspect of the Inspection and Test Plan shall include as a minimum:

All tests required by relevant Standards;

Location of manufacture;

Scope of activities undertaken at the facility;

Review of production machines and key components‘ suppliers and certifications;

Materials/Equipment supply contracts;

Technical review of materials/processes;

Review of certifications for bill of materials, and in particular, confirmation that they relate to the bill of materials to be used for the relevant production run;

Factory quality: including processes, certifications, quality control, levels of automation and staffing, safety records, ingoing and outgoing QA procedures and production tolerances;

Quality control criteria and processes, including track record of warranty claims;

QA statistics and recall volumes including reasons for recall (e.g. materials, manufacturing, design, shipping), including outcomes of recall process;

Factory inspection and acceptance testing of components to be shipped, included procedures for rejection of equipment in the event that faults are identified;

Finished goods management including sorting and packaging procedures for the relevant Materials; and

Type test certificates for the combiner boxes, string inverters or inverter stations, AC isolators, transformers and switchgear shall be provided to show compliance with the Relevant Standards.

The Employer’s Representative with the Contractor support shall witness and approve the FAT.

### Pre-Shipment Factory Testing and Inspection

The Contractor shall undertake pre-shipment testing and inspection upon completion of manufacture and prior to shipping. The Contractor shall submit a FAT schedule to the Employer and confirm the actual date 2 weeks before the FAT happens, allowing the Employer or the Employer’s Representative to witness the FAT.

Factory Acceptance Test (FAT) certificate completed during the manufacturing assembly and testing of inverter station equipment, power stations, solar PV modules, HVAC, fire detection and suppression system, cables, switchgears, substation equipment, SCADA, protection panels, transformers, steel works and module structure shall be forwarded to the Principal Designer for approval.

Pre-shipment acceptance criteria of the major equipment manufacturers shall be in the ITP.

As an example, the pre-shipment testing of PV modules shall incorporate the following tests, in accordance with IEC 61215, to be completed on a 100% sample:

Visual inspection;

Electroluminescence (EL) testing;

Maximum power determination or ‘flash’ testing; and

Insulation test.

The Contractor shall supply the Employer with Test Results for the above-mentioned tests that shall include flash tests results and electroluminescence images in electronic format for all modules.

Gel contents tests shall be performed on a sample of Modules.

A complete description of the pre-shipment testing is included in the Technology Specific ERs .

## Plant Commissioning Tests

Commissioning is a systematic process of ensuring that the systems perform according to the design intent and the future operational requirements. All equipment and systems should be installed, assembled and tested according to manufacturer’s recommendations and the best practices and standards of the industry.

The commissioning process involves:

Integration of each sub-system to work with its interfacing sub-systems;

Testing of each sub-system and then the complete system to demonstrate that they meet their requirements; and

Commissioning of each system together with the systems of Others where they interface so as to bring the system whole into operation.

The HV switchgears and grid connection tests will be orchestrated by the Contractor or any ICP Subcontractor, with all supporting tests and hot commissioning activities of the generators adhering to the testing schedule governed by  the Contractor or any ICP Subcontractor, with inputs from the Contractor.

The commissioning tests are performed to determine and verify the proper operation of the Plant and all its sub-system components.

The commissioning guidelines described hereby are technology specific. General commissioning tests requirements are described in section 10.6

The commissioning works will be carried out in phases:

Phase 1, Mechanical completion as minimum the following test shall be completed

Factory acceptance tests

Installation release tests 10.2;

Phase 2, Pre-commissioning test 10.5, as well as per Technology Specific ERs;

Phase 3, Energisation and commissioning 10.6, as well as per Technology Specific ERs.

Each phase will produce test datasheets and reports which will be made available to the next phase in order to minimise re-testing. All the test listed into this section shall be performed by the contractor which can optimise the logic and the sequence of the testing.

All the Tests shall be listed on the test schedule, included in the inspection and test plan (section 5.2). The Employer or the Employer’s Representative must be made aware when the Tests will happen and has the right to witness.

The Equipment shall be tested at Site. These tests shall prove whether the equipment meets the requirements and the safety conditions, whether it has been built and/or erected with satisfactory workmanship and whether the equipment is in conformity with the prevailing Standards and Regulations, the manufacturer's recommendations and installation/ commissioning procedures and with the present state of modern technology.

# Site Specific Details

## The Site

The Site is detailed within tables and maps in this Section 3.1.

Table 2: Site Description

|  | Description |
| --- | --- |
| Site Name | Hessay Solar Farm |
| Location Description / Address |  |
| Coordinates |  |
| Area (Hectares) |  |
| DNO |  |
| Connection Voltage (kV) | 33V |
| Export Capacity | 49.16MWp |
| POC type and Location |  |
| Approximate Cable length (POC to substation) | 6KM |
| Ground Conditions | Topsoil & Clay “see attached GI Report” |
| COD |  |
| Planning permission status | Full planning permission granted |
| Lease status |  |
| Access route | See Attached CTMP |

INSERT maps showing:

Proposed And temporary access points

Site boundary and site access points

Grid co-ordinates

### Employer provided documents

The Contractor shall be responsible for verifying and interpreting all such data (as contained in the studies, surveys, etc. provided by the Employer) and for properly taking into account all Site Conditions in the execution of the Plant. The Employer shall have no responsibility for the accuracy, sufficiency or completeness of any data, surveys, studies and reports provided to the Contractor, and these surveys are not to be considered reliance material, save as otherwise specified in the Contract.

The Contractor shall, as a minimum, prepare and complete its own surveys, studies and reports as specified in Section 2.7 in addition to any other survey, study or report not listed in Section 2.7, but necessary for the proper execution of the Plant in accordance with the Contract.

## Site Conditions

## Save as regards Unforeseen Site Conditions, the Contractor shall be responsible for identifying and fully detailing all relevant Site and climatic conditions applicable to the Plant and documenting these conditions in a Site Conditions report to be submitted within four (4) weeks of the Notice to Proceed. The Contractor’s assessment shall be based on its own assessment and investigation as to the most severe climatic conditions or local regulations which should be used as a basis for the final design of the Plant.

## Technology Specific Scope of Work

This section details the specifics of the Contractor’s scope of Work in relation to the Project. The Contractor’s general scope of Work is detailed in Section 2.

The PV and ICP specific Engineering Requirements have been split from this General Engineering Requirements document. These documents are referenced as such:

PV Technology Specific ERs;

ICP Technology Specific ERs.

# Project Management

Until Completion the CDM compounds shall be managed solely by the associated Contractors.

PV Contractor will manage the PV area (denoted in COLOUR…) and all associated welfare facilities.

The ICP Contractor will manage the Grid Compound and HV switchgears / Ring Main Unit (RMU) (Grid Compound included in the X location of the COLOUR region…). The ICP Contractor will also be responsible for the cable connection via the route indicated in gold on the map.

INSERT General Plant Layout denoting areas of work and welfare locations COLOUR).

The Contractor shall utilise its extensive project management skill, experience and resources to appoint a competent team for the successful execution of the each Facility that is part of the Plant.

Key project management activities of the Contractor shall include:

Responsibility for all engineering, procurement and construction aspects of the Facilities ensuring that the Contractor’s individual activities are compatible with each other and with the overall Schedule and Milestone Schedule;

Ensuring that each Facility and the overall Plant is technically integrated and cohesive;

Ensuring that all documentation is to a common format and style of presentation and is competently rendered in the English language;

Applying technical control to ensure that a consistent approach is adopted by all the Contractor’s engineering teams (including Subcontractors); and

Ensuring the cohesive, accurate and timeous provision of documentation in support of review processes, construction activities, commissioning processes, testing processes - all within the timescales agreed as per the Schedule and Milestone Schedule.

## Planning and Coordination

The Contractor shall prepare a project execution plan outlining how it intends to execute the Plant The plan shall include all major elements of the Plant and each Facility including project management and control, engineering design and technical coordination, procurement, point-of-manufacture inspection and testing, construction including pre-commissioning, commissioning and training required for the Plant. The plan shall include an interface management plan, with detail of authority management, outlining how the Contractor will manage and coordinate interfaces among parties involved in the Work including subcontractors (including ICP Contractor), equipment suppliers and the Employer.

The Contractor shall undertake, as a minimum, all of the following services.

Project management, including project administration, scheduling, cost control, and Quality, Health, Safety and Environment (SHEQ) management;

Conduct reviews and incorporate outcome of reviews such as constructability, operability, accessibility, maintainability at appropriate stages of the design process and fully document and provide reports regarding these reviews to the Employer;

Lead and participate in design, coordination and progress meetings with the Employer (and its engineers), Energy Market Operator or any other party as required;

Technical support for the Employer’s permitting and licensing activities including compliance with all relevant requirements of the Employer’s Permits;

The planning and design of the Work; and

Coordinate all work with others as required including its Subcontractors, the landowner, the Employer and the Employer’s personnel, the Energy Market Operator and any other affected parties.

## Procurement

The Contractor shall be responsible for the overall management of procurement, including expediting, and QA/QC with respect to all elements constituting the Facility.

The Contractor shall, in order to satisfy the requirements contained in this ERs, identify the manufacturers and places of manufacture and ensure appropriate testing and inspection of major equipment (i.e. modules, inverters, AC isolators, transformers, [trackers/mounting structures], drives, controls etc.) and switchgear before dispatch to Site. The Contract contains a list of pre-approved Subcontractors to be used for procurement of major equipment. Any equipment should be from manufacturing lines with inputs that are traceable, and prioritisation should be given to supply chains that promote avoidance of labour or materials from high-risk areas with regards to forced labour / child labour practices and higher environmental damage. A preference should also be given to using suppliers that hold ESG certification from a recognised independent body covering labour and environmental practices. The Contractor shall obtain Employer approval for the use of any other Subcontractor for major components or where the subcontract value is above GBP one [1] million.

Where major equipment is yet to be manufactured the Contractor must promptly alert the Employer, accordingly, supplying the anticipated manufacture dates so that the Employer may (at its sole discretion) inspect the point of manufacture prior to manufacturing beginning.

Unpriced copies of purchase orders shall be expeditiously provided to the Employer if requested.

## Construction Management

The Contractor shall be responsible for the overall management of the Facilities and the overall Plant and operation and maintenance until Completion. These services include but are not limited to:

Management of the Contractor’s staff and its Subcontractors;

The provision of suitable and adequate security for the Site for the duration of the construction period and until Completion;

Conducting risk assessment and implementing resulting mitigations for all activities related to the Works;

Provision of construction power, water, fire protection, lighting, compressed air, telephone, data transmission and sanitary facilities;

Construction of all necessary access roads and roads on Site and reinstatement of existing roads after the construction, if required;

Provision of all required tools, components, machinery, and test equipment;

The positioning of the component parts forming part of the Plant, such that they can be operated and maintained in a safe manner wherever possible without requiring specialist Third Party equipment to access, operate, maintain, exchange, or replace. For example, inverters should be placed in an easily and safely accessible area;

The supply and transportation of all components constituting the Plant to the Site and to the specific installation locations;

Transportation, handling and installation methodology of all components which is in line with manufacturers’ recommendations and which does not compromise the integrity or warranties of any components;

Equipment and materials-receiving, handling, laydown areas and storage (indoor and outdoor as required). No additional land will be provided by the Employer for laydown beyond the boundaries of the Site;

The construction and foundation of all supporting or mounting structures as necessary;

The assembly and installation of the components;

The installation of an approved energy meter and associated communication equipment;

The registration of the Plant with any applicable authorities, industry bodies, etc;

The design, installation and integration of the Plant earthing and bonding systems;

The design, installation and integration of the Plant lightning protection systems; and

Coordination and cooperation with the party responsible for the Grid Connection Works to facilitate the connection of the Works to the Grid.

## Progress Reporting and Meetings

The Contractor shall produce weekly and monthly progress reports, at dates to be agreed with the Employer. Reporting requirements may be appended to this ERs.

The Contractor shall attend monthly site meetings along with any other meetings necessary to complete the Works or reasonably required by the Employer.

# Quality Assurance/Quality Control (QA/QC)

The Contractor shall be responsible for implementing its Quality Plan, including, but not limited to design, construction, transportation, storage, installation, materials, equipment, checkout, start-up and operation until the Contractor has discharged its obligations in terms of the Contract.

As a general practice, the Contractor shall have established project management systems for quality management that have been certified to ISO 9001. The Contractor shall use these as the basis for developing a project-specific quality plan to cover all stages of the Project and Site environmental management plans which shall be compatible with each other.

The Project Quality Plan shall include a QA/QC manual applicable to the scope of the Contract covering design, procurement, construction, Testing and start-up of the specific technology. The Quality Plan shall be subject to reasonable audits by the Employer or Employer’s chosen representative. The Employer shall maintain the right to identify and request updates to the Project quality plan as a result of the audits, derived from the coordination with the rest of SoW of the Plant. The Contractor shall work diligently with Subcontractors to address the Employer’s reasonable requests.

The Project Quality Plan shall include a section for Non-Conformance management requirements, setting a clear Non-Conformance Reporting (NCR) management procedure covering as minimum:

- NCR classification procedure

- Timescales for investigation and remediation

- Root Cause analyses (RCA) requirements

- Two-party sign off and closure procedure

The Quality Plan shall be enforced to assure that the Works are conforming to the Contract requirements and shall include as a minimum:

Contractor’s quality policy and project-specific quality objectives, including identification of key quality risks.

Project organisation chart defining QA/QC roles and responsibilities.

Definition of interfaces between design, procurement, construction and commissioning quality controls.

Records management, document control and retention procedures, including maintenance of a quality records register and documentation of all changes to drawings and specifications.

Full Inspection and Test Plan (ITP) for the Works, including defined Employer hold and witness points.

Audit and surveillance programme.

Control and qualification of subcontractors and material vendors in accordance with technical specifications, including QA flow-down requirements.

Factory inspection and testing, including module factory inspections, flash test data review, and factory quality acceptance standards.

On-site material inspections and material acceptance testing where required (e.g. concrete, steel, specific components).

Field quality inspections and testing, including coverage of electrical works and associated field testing documentation.

Management of defects, deficiencies, non-conformances and punch list items, including the NCR process with classification, timescales and escalation procedures.

Sampling procedures for Testing shall follow the international norm ISO 2859:1999.

The Contractor shall develop and maintain a record of defects, deficiencies and non-conformances identified during construction, which shall be included in weekly progress reports.

The rejection criteria for major equipment delivered to the Site shall be equivalent to the factory-leaving acceptance criteria.

## Factory Acceptance Tests

All goods, Materials and other items forming part of the Plant shall be tested in accordance with Law, Permits, Standards and the Quality Plan. Quality checklists and test protocols shall be submitted to the Employer prior to factory tests.

Further requirements for Factory Acceptance Tests are contained in Section 2.24 and Technology Specific ER documents.

## Inspection and Test Plan

The Contractor shall submit a Site Specific ITP covering the whole of the Works within 60 days of Notice to Proceed. The Inspection and Test Plan means a document detailing all inspections and tests to be performed by the Contractor, Third Party auditors and the Employer, in order to ensure that the Plant is completed in line with requirements of the Contract. The Inspection and Test Plan will include an overview of all tests to be performed, along with detailed test sheets which will be completed during each test or inspection and the acceptance criteria, . All test sheets will be provided to the Employer once relevant tests are completed. The ITP shall be provided in order that the Employer can confirm all tests are being performed to Contract requirements and attend relevant tests.

Further ITP requirements are contained in Section 10 and Technology Specific ER documents .

    - Notice of Inspection and Test

When monitoring, witness or hold points (inspection points) for quality surveillance or tests require the presence of the Employer, the Contractor must give notice by email, at least 5 working days prior to each inspection point which requires attendance by the Employer.

For major inspections requiring off-site resources of the Employer (like FATs), the Contractor shall provide indicative timing at least 20 working days in advance, with the date confirmed at least 10 working days in advance.

    - Records

The Contractor must retain sufficient records as objective evidence to assure that the Contract requirements are being met and that the quality system conforms to the nominated quality management system standard. A register of those records must be maintained.

These records must be made available for verification of payment claims. Originals of documents must be provided for examination on request and copies submitted where required.

Records shall include information on key components and associated BoP, including items such as:

- Serial number of components and location;

- Commissioning date; and

- Notable events and incidents.

The Contractor shall retain records as objective evidence to assure that the requirements for Defects identification and notification are being administered in accordance with the quality management system standard.

The Contractor must retain the quality records for the Contract for a minimum period of 5 years.

# Health and Safety Plan

The Contractor’s Health and Safety Plan shall document which relevant and current Health and Safety Law and requirements the Plant falls under and will describe how the Contractor will ensure the Works are completed in line with such Law, requirements and good industry practice. The contractor and all employees shall be compliant with the HSE 1974 at Work Act under UK law. This also includes compliance with Electricity at Work Regulations 1989 Act and the Construction Regulations HSE 1996 Act.

The Health and Safety Plan shall include a Health and Safety policy defining the Contractor’s commitment to Health and Safety matters to the satisfaction of the Employer.

The Contractor acknowledges is responsible for:

Promoting and maintain a safe working environment, implementing the Employer’s Zero Harm policy in the Contractor’s SHEQ policies;

Management and control of all Works carried out on the Site and the supervision of all employees and Subcontractors on the Site;

The safety of all personnel on the Site;

Management and regular review and updating of all Health and Safety documentation, including sub-contractor risk assessments and method statements;

Provision of all personal protective equipment and clothing required to comply with all Health and Safety legislation;

Providing induction and appropriate training of all personnel attending site and maintain appropriate records;

Immediate notification (to the Employer and relevant authorities as applicable), investigation and reporting of all incidents that caused or could have caused injury to personnel or caused damage to equipment or structures on the Site;

Provision of first aid facilities and trained first aid personnel on the Site at all times that work is being carried out; and

Developing, tracking and review of Health and Safety key performance indicators.

The Contractor shall prepare and implement a Quality, Health, Safety and Environment (‘SHEQ) policy and associated procedures which will apply at all times during the design, preparation, construction and operation of the project.

The Contractor shall act as the “Principal Contractor” upon award and throughout the pre-construction and construction phase of the Project for the purposes of the Construction (Design and Management) Regulations 2015 (the “CDM Regulations”) and shall be responsible for the implementation of the necessary working practices, procedures and risks assessments. Section 2.16 provides more details on CDM Regulations.

  - Minimum PPE Requirements

The Contractor is responsible for the provision of all Personal Protective Equipment (PPE) required by its employees for the safe execution of the Works and in accordance with the national laws and regulations of UK. Toxic materials such as asbestos are strictly prohibited.

The Contractor will provide, install and maintain any necessary barriers, warning signs and other such safety equipment as is required.

The following PPE shall be the minimum requirements for all personnel on the Site:

- Steel toe capped boots (no exposed steel);

- High visibility jacket/apparel;

- Hard hat (undamaged and identifiable issue date);

- Safety eye wear (as required);

- Work gloves to be available to all personnel for use as required;

- Hearing protection (as required);

- Face mask/ screen (as required); and

- Dust mask (as required).

Any additional specialist PPE required by the Contractor’s personnel to carry out the Works shall be made available by the Contractor as required by the Contractors Health and Safety Plan.

## Incident Reporting

The Contractor must notify the Employer, and any other parties nominated by the Employer, of any incident involving injury, property damage or environmental damage, any near misses and all hazardous observations. The incident reporting procedure shall be defined in the Health and Safety Plan.

The Contractor must ensure that all reportable incidents are reported to the relevant authorities immediately or as required by Law.

## Hazardous Areas

Areas where a potential flammable atmosphere may exist shall be classified to the relevant sections of Law, Permits and Standards.

Only suitably certified equipment shall be kept or used in designated hazardous areas. To the maximum extent practicable, equipment requiring operator attention and/or electrical equipment shall not be installed in hazardous areas.

The Contractor is required to demonstrate in the Plant design that adequate segregation of electrical equipment from hazardous areas has been made, and that no hazardous area extends beyond the Site boundary fence.

## Fire Protection and Fire Fighting Systems

The fire alarm and detection, fire protection and firefighting systems shall accord with recognised good practice and shall comply to all applicable Law, Permits and Standards.

The Plant shall be designed, installed and commissioned so as to ensure a safe operating environment for equipment and personnel. This shall be achieved through the separation and segregation of equipment with sufficient distances and by the selection of suitable equipment and materials with respect to their intended purpose. A reasonable degree of self-sufficiency shall be designed for, taking into account the location of the nearest fire department or formally constituted and adequately maintained and resourced fire-response cooperative.

Hazardous areas shall be identified, and suitable equipment shall be selected for use in such areas. Different firefighting systems shall be adopted according to the operational characteristics of the particular Plant areas and buildings to be protected.

For the protection of personnel and the Works the Contractor shall ensure adequate on-site fire-fighting facilities and water storage are available on the Site. The Contractor shall liaise with local authorities so as to inform themselves of requirements, capability, fire prevention practices and in order to determine the scope of the facilities to be provided.

Notwithstanding the requirements outlined above the Contractor shall:

Conduct a fire risk assessment in accordance with good industry practice and applicable to both construction and operation of the Work;

Design, plan, construct, test, commission and operate the Works in such a way as to minimise the fire risk of the Work;

Ensure that the Site and Work is suitably equipped to respond to any fires on site;

Notify the relevant local emergency management committee following construction of the Works, and prior to the commencement of operations; and

The Emergency Response Plan shall identify fire risks and controls, and procedures that would be implemented if there is a fire on site or in the vicinity of the site.

  - Noise Limits

The Control of Noise at Work Regulations 2005 is a national policy based on the EU Directives and designed to promote an environment free from noise that may impact health and welfare. The Act recommends maintaining environmental noises at 80 dB(A).

The contractors are required to comply with the following:

Assess the risk of the employees from noise at work;

Ensure preventative measures are in place to reduce any noise impact;

Provide correct PPE (hearing protection) if noise exposure is not reduced to a suitable level;

Ensure the legal limits on noise exposure is not exceeded;

Ensure employees are provided with information, instructions and training; and

Carry out health surveillance where there is risk to health.

Exposure to loud noise (over 85 dBA) should be limited as much as possible and construction workers should use protective gear (PPE) when working in a noisy environment e.g., hearing protection device. It is recommended that the site has sound barriers erected (when necessary) to protect residential properties from noise exposure during construction work. There should also be a competent individual (part of the EPC) to overlook on-site safety and all noisy work should be scheduled to limit exposure. In addition, where possible the use of quieter or noise cancelling equipment is encouraged.

Table 4: Noise Levels

| Exposure Action | Values |
| --- | --- |
| Low Exposure (Daily or Weekly) | 80 dB(A) |
| Low Exposure (Peak Sound Pressure) | 135 dB(C) |
| Upper Exposure (Daily or Weekly) | 85 dB(A) |
| Upper Exposure (Peak Sound Pressure) | 137 dB(C) |

Noise values of 87 dB(A) and Peak Sound Pressure of 140 dB(C) should not be exceeded. Where the letters "A" and "C" refer to different frequency weightings. dB(A) uses an A-weighting filter that mimics the human ear's sensitivity to various frequencies, making it suitable for general noise assessments and potential hearing damage evaluation. dB(C) employs a C-weighting filter that captures more low-frequency sounds and is used for measuring peak sound levels.

In the event that the Works are found to exceed the noise level required in the Development Approval conditions or found otherwise unacceptable to the Planning Authority solely on the basis of noise, the Contractor will work diligently with the Employer and the Planning Authority to design and implement acceptable noise mitigation. Such additional mitigation will be handled as a variation to the Contract.

# Environmental Plan

The Contractor shall operate an industry standard environmental management system in line with ISO 14001 and the Environmental Act 2021. The Contractor's Environmental Plan shall document how the Contractor will ensure compliance with all statutory obligations, including Law, legislation, and requirements of Employer’s Permits and Contractor’s Permits. The Contractor shall, to the greatest extent possible, complete the Works to minimise disruption and damage to the environment and minimise where possible the impact of the Plant on the environment.

The purpose of the environmental plan is to ensure that the planned development is in line with the environmental legislation. It should highlight the EMS requirements, provide mitigations techniques within the Environmental Statement that will be implemented on site and provide necessary method statements.

As per the Act 2021, the following subject areas should be covered in the Environmental Plan:

Air Quality;

Water Quality and Drainage;

Noise and Vibrations;

Landscape and Visual Impact;

Archaeology and Heritage;

Waste;

Energy;

Transport; and

Geology and Soil.

Under the Environmental Act 2021, the Contractor is required to comply with all regulations for waste disposal. For electrical and electronic waste management, the UK has specific requirements under the Waste Electrical and Electronic Equipment (WEEE) Regulations that the contractor shall comply with.

# Design Requirements

## General

The Plant shall be designed for 40 years’ continuous performance of its intended function from first export of electricity with respect to Site Conditions and anticipated operating conditions (including but not limited to lightning prevalence and severity, ambient temperature, soil, flooding, dust and mud, irradiation, grid conditions, and altitude) based on regular scheduled/preventative maintenance being performed.

The designs, components and materials to be used by the Contractor shall be of proven quality and shall have been used in international non-recourse project-financed projects. The Plant design shall consider future safe and economical decommissioning and Site rehabilitation without undue harm to the environment.

The systems shall be designed and optimised in such a way as to minimise the losses due to shading, soiling, DC & AC cable losses, inverter losses, mismatch and transformer losses. In particular:

The array cabling network must be designed to ensure that the total cable losses (DC & AC) are less than 2% in average for the total array cabling network, as a percentage of total generated energy;

The HV transformer losses must be less than 1.3% for annualised electrical losses in average as a percentage of total generated energy;

The LV/HV transformers shall not contribute more than 1.3% power loss while in operation;

The calculation of electrical losses shall consider the expected irradiance for the PV Facility; and

The loss calculation shall include all assumptions made and be provided to the Employer for review.

Auxiliary loads shall be kept to a minimum, particularly during non-generation periods.

The Plant shall be designed such that normal operation of the Plant shall not create risks to operations or maintenance personnel. The Plant shall incorporate all SHEQ elements required and in accordance with good industry practice, including, if required hazard identification sessions.

## Design Review by Employer

During the course of the engineering, procurement and construction of the Plant, the Contractor shall submit design documentation for review by the Employer. The documents and drawings listed in Section 13 should be used as an indication of design documentation to be produced and reviewed.

The Contractor shall maintain a document management system and tracker sufficient to identify status and revision numbers associated with the document.

As part of the design packages the Contractor shall submit detailed design reports including specifications and drawings to the Employer for review, comment and approval. The scope for the design report shall cover design input, design output, design reviews, design verification and design validation to ensure compliance with the Contract. The Contractor shall provide the Employer with not less than five (5) Business Days’ notice in advance of submitting the relevant design package. The Employer shall review the design package and provide comment within 15 Business Days.

The Contractor is to ensure that all documentation submitted to the Employer is complete and has been subject to the Contractor’s review and approval process as documented in its Quality Plan.

All comments made by the Employer are to be addressed by the Contractor to the satisfaction of the Employer and relevant documents or drawings shall be re-submitted so that the Employer may assess the adequacy of the revised submissions. For the avoidance of doubt the Employer’s right to comment on design documentation does not transfer any responsibility to the Employer, and the Contractor shall ensure the Facility is designed in line with requirements of the Contract.

Documents and designs shall be submitted electronically in both editable (native) and PDF formats. Drawings shall be provided in an editable AutoCAD DWG format so as to enable reproduction of drawings and PDF, unless otherwise agreed in writing.

All drawings shall be unique to the Plant and not typical or indicative.

## Civil And Structural Works

The Contractor shall be responsible for all ground risk in accordance with the Contract including the design and construction of foundations, drainage and subsurface works suitable for the actual geotechnical conditions of the Site.

The Contractor shall be deemed to have satisfied itself as to the ground, groundwater and contamination conditions at the Site.

The Contractor shall be responsible for validating and, where necessary, supplementing available ground investigation data.

The Contractor shall be responsible for:

- the design and construction of all foundations, plinths, slabs, earthworks and substructures required to support permanent and temporary loads;

- the design and installation of permanent and temporary surface water and subsurface drainage systems;

- groundwater control, dewatering and protection against flooding during construction and operation;

- Temporary works design to be undertaken;

- All civil and structural works to comply with applicable British Standards, Eurocodes, statutory requirements and local authority approvals.

### General Characteristics

Civil works shall include but not be limited to the following items:

Site investigations and surveys;

Conservation and re-use of topsoil;

The establishment of all necessary access roads to construct, operate and maintain the Plant, including permanent access to the Plant;

Site preparation: site clearance, earthworks, excavations, fillings, and levelling;

Foundation and structural systems;

General buildings and all electrical and mechanical buildings;

Furnishing and equipping of all buildings required for operation and maintenance of the Plant (e.g. tables, chairs, cupboards, etc.);

Storm-water drainage systems;

Sewers and sewage systems;

Water supply and storage – if applicable;

Road crossings and directional/horizontal drilling as required;

Electrical and earthing trenches;

Ducts and ducting;

Parking lots, storage areas;

Fencing, gating and access control;

Landscaping and establishment of appropriate low-maintenance groundcover;

Any further civil works arising out of the Employer’s Permits;

Maintenance until Completion is achieved;

Rectification of defects;

Temporary buildings (e.g., offices for the Contractor);

Temporary roads and parking and laydown and storage areas;

Temporary fencing, lighting and security for all materials;

Reinstatement of access roads outside the Site area; and

Reinstatement, and where appropriate, rehabilitation of the Site.

Any temporary work shall be promptly removed by the Contractor before Completion or upgraded to meet requirements for permanent civil works as part of the scope of works.

### Access Roads, Parking Areas, Other Areas

Internal roads, parking areas, and other surfaces within the Site shall be the responsibility of the Contractor.

Internal roads shall be planned and constructed according to the Plant configuration proposed by the Contractor and shall be adequate and suitable for the operation and maintenance activities that will be required for the design life of the Plant.

All surfaces shall be designed to allow proper drainage. The drainage system will be designed such that water drains away from key components following periods of rainfall. The drainage system shall be designed in a manner such that other infrastructure (such as trenches, ducts or cable conduits) does not act as part of the drainage system. The drainage system shall also comply with the requirements stated by the local authorities.

Surfaces shall be designed to support the use of heavy vehicles needed for the transportation of goods and Materials to and within the Site during the construction and operations phases of the Plant. Heavy vehicle loading shall be analysed based on a Plant specific analysis of vehicle movements over the construction and operations phases. Roads and parking areas shall be designed to suit Site Conditions and the findings of the Geotechnical Report. Compacted crushed rock shall be used as a construction material if periods of wet weather are anticipated.

All buildings and surfaces to receive equipment shall be designed with appropriate specifications to manage flood risk, including height above ground level. If required, a flood risk assessment shall be produced to confirm flood resistant design criteria are appropriate.

Roads and surfaces shall be designed in conformity with a specialist geotechnical report procured by the Contractor. When compliant with the structural requirements, locally available material shall be used. Road surfacing shall mitigate against potential module damage or soiling caused by traffic. Roads shall provide easy access to all the SCADA boxes, tracker drives (if the Plant uses trackers as mounting structures), inverters, AC isolators, transformers, substation, and permanent buildings, located within the Site.

Road width (the usable surface) shall be at least 4 metres for internal roads and 6 meters for main site access road, or as per relevant local requirements. The turning radius shall be sufficient to allow access for maintenance and replacement of the largest components and for emergency personnel, including lifting and replacement of heavy components that may be pre-assembled in factory and transported, lifted and placed on site by means of heavy-duty cranes.

Dust control measures are to be implemented during construction as well as permanent measures at the end of construction to minimise dust during operation and maintenance activities.

Parking and storage areas sufficient for operation and maintenance of the Plant shall be foreseen and provided.

### Foundations

Prior to construction the Contractor shall carry out all necessary geological and geotechnical investigations and studies so as to satisfy itself of the ground conditions.

In the Contractor’s calculation notes and drawings, the following information, as a minimum, shall be made available to the Employer:

Detailed foundations characteristics (type, dimensions);

Reinforcement characteristics (diameter, steel grade, protection against corrosion);

Concrete characteristics (grade, composition); and

Static and (if applicable) dynamic calculations.

Foundation surfaces shall be carefully finished, and all concrete works shall be floated and have bevelled edges.

#### Other Foundations

The Contractor shall provide a detailed structural analysis demonstrating that the design conforms to the Contract and shall clearly state in the report the load assumptions and the design specifications.

Foundations shall be designed to withstand the Site Conditions for the entire lifetime of the Plant, without being replaced.

In designing the foundations, the Contractor shall take into account the loads the foundation will be subjected to. The foundations shall be able to transfer all actual load combinations, including horizontal and uplift forces, safely to the foundation system with a suitable factor of safety.

Platforms for oil-filled step-up transformers shall include an oil spill containment basin and shall allow for oil-water separation. Bunding shall be provided for 110% of the full volume of oil contained in the equipment placed on the foundation or be designed as required by local regulations.

### Structural Design Principles

All structural design reports, calculations and drawings prepared by the Contractor shall be signed by a certified structural engineer as being appropriate.

Dynamic loads shall be considered when these might lead to higher stresses than static loads, and these shall be estimated using state-of-art tools and methodologies. A modal analysis shall be performed when necessary.

Fatigue verification shall be performed should fatigue be considered as critical for the component under evaluation. Estimations shall be performed using state-of-art tools and methodologies.

### Load Assumptions

In designing the Plant, the Contractor shall take into account all the reasonably expected loads that the Plant might be subject to, including, but not limited to:

Self-weight loads;

Transportation and handling loads;

Construction loads;

Wind loads;

Thermal loads;

Snow loads;

Seismic loads; and

Water (flooding) loads.

The Contractor shall consider the loads and load combinations as applicable to the Site.

The Contractor is responsible for system survivability over the design life of the Plant.

All components shall be designed or verified against ULS load combinations expected over a return period of no less than 50 years.

### Wind Loads

The Contractor shall verify the suitability of the structures and components for the Site Conditions and shall document the assumptions made.

Each component forming part of the Plant shall be designed or verified for the expected wind loads. This includes, but is not limited to, foundations, buildings, modules, trackers, towers, weather stations, fences etc.

The Contractor shall perform its own investigation as to the maximum expected wind conditions over a return period, in any case not less than 50 years.

Wind induced vortex shedding shall be taken into account and checked against the frequencies of the structure. Wind-induced dynamic instability shall be avoided.

Wind loads shall be duly combined with other loads by implementing adequate safety factors.

The Contractor shall seek to support its assumptions and calculations using wind load tests, such as wind tunnel tests or computational fluid dynamics tests whenever necessary to demonstrate compliance with the Contract.

### Seismic Loads

The Contractor shall perform its own investigation as to the maximum expected seismic accelerations over a return period compatible with the Design Life and use of the Plant.

The Contractor shall duly document the assumptions made using available measurements and any supporting material verifying the suitability of the structures and components to the Site Conditions. Each component forming part of the Plant shall be designed or verified against the expected seismic loads.

Seismic loads shall be combined with other loads by implementing adequate safety factors.

### Civil Construction Material

Materials selected by the Contractor shall be proven to be suitable and sufficient for the Plant design life. In particular, structural steel will be procured in line with all Applicable Laws and Standards, and concrete testing shall be performed in line with local requirements.

## HV AC Works

HVAC works shall be designed in accordance with the requirements of equipment manufacturers and the Contract, accounting for local ambient conditions over the Plant design life.

The internal HV RMU switchgear shall be at [X]kV.

The connection to the grid shall be at [X]kV.

## Electrical Works

All electrical equipment shall bear nameplates according to international and country-specific requirements. All materials shall be of high quality and shall be supplied by leading manufacturers that are capable of providing material in accordance with international good practice. Special care shall be taken to choose equipment that is backed by reliable support and maintenance in United Kingdom.

Voltage insulation levels, earthing, and protection schemes shall be coordinated in conjunction with the requirements of National Grid and relevant British Standards, and all relevant transmission, distribution, and grid code requirements. Consequently, the Contractor is responsible for conducting all electrical studies required to ensure compliance to National Grid’s connection requirements.

Protection studies are to be carried out to address the following and shall establish suitable relay settings, as necessary, including:

Overcurrent and earth fault relay co-ordination with grading curves;

Overload protection;

Differential and restricted earth fault protection;

Bus bar protection;

Over-voltage, under-voltage protection;

Over-frequency, under-frequency protection; and

Anti-islanding protection.

Protection studies and system studies shall cover all equipment and systems including but not limited to PV modules, combiner boxes, inverters, MVS, HV system including switchgear and cabling, all auxiliary systems, DC systems, UPS systems, earthing and bonding systems, lightning protection systems, building services, and connection compliance equipment (if required), etc.

The Contractor shall complete a harmonics study that demonstrates compliance to harmonics limits using measured background harmonics data is provided. If non-compliance is shown the Contractor shall identify the remediation.

All high voltage and low voltage switchgear, DC equipment and AC equipment shall be designed with respect to the Site Conditions and shall be equipped to withstand high amounts of dust in the air.

The electrical system shall be controlled and monitored through the SCADA system.

The Plant is to be equipped with a low-voltage system for powering:

Buildings and support facilities;

Lighting;

SCADA System;

Security system, including CCTV and Intruder Alarms;

Meteorological stations; and

Fire Protection and Alarm systems.

All electrical installations are to be installed in a neat manner in order to facilitate access during operations, and ease trouble-shooting and maintenance activities.

The Contractor is responsible for the supply, installation and termination of a complete electrical system and the Facility must be designed in such a way as to include the following:

Meet the requirements of the Connection Agreement;

Passive and active inverter anti-islanding protection built into each inverter;

Independent backup power for protection devices;

Trip circuit continuity, monitoring and fail alarming;

All equipment shall be rated for full load and the maximum prospective fault current levels;

Co-ordination with upstream protection;

Auto-restarting of the inverters following interruption of grid supply, where permitted;

Earthing for substations, inverters, array and array frames, fences and other structures as required;

SCADA requirements;

Inter-trips signals from the GNSP (where required);

Revenue metering;

Plant auxiliaries supply including auxiliary transformers, HV switchgear, LV switchgear, HV/LV bus ducts and cables, DC and UPS systems, lighting;

Remote monitoring system of the PV system;

Electrical building services to all buildings;

Security and surveillance systems and equipment;

Access control system; and

Site lighting.

### P28 and P29 Modelling Package

- Detailed design inputs are to be incorporated into the Harmonics Study models as required by National Grid under the Connection Agreement.

- The Contractor or any ICP Subcontractor is to lead on the National Grid connection procedure, including BEGA compliance and certifications.

- The Contractor will assist whenever asked in the connection procedures, including support with paperwork, models and testing/commissioning activities.

# Equipment And System Requirements

## General

All components and equipment provided shall be suitable for installation at the Site. The Contractor will bear responsibility for assessing and accommodating for the Site Conditions.

The Plant equipment shall be designed, transported, stored, and installed or constructed in compliance with all component manufacturer installation guidelines ensuring that all warranties and guarantees are maintained intact. The Contractor shall, during the execution of the Plant, adequately protect all equipment and materials against exposure to adverse environmental conditions.

Major equipment components (not limited to PV modules, inverters, AC isolators, transformers and switchgear) shall be of high market standard and proven technology, being a technology/product that has been installed (included tested, commissioned and operated) at international non-recourse project financed projects of similar size and complexity to the Plant.

The Contractor must ensure all equipment shall be maintained in a climate-controlled shipping enclosure and protected from the weather during all the processes under its responsibility, including manufacturing, end of line storage, shipping and delivery to site. The Contractor will be responsible for unloading, erecting and installing all the equipment, as well as for storing and keeping it in site. The equipment shall be stored in the temperature and humidity range specified by the OEM of each component. The Employer retains the right to reject any equipment that has been damaged during transportation. Detailed equipment inspections will be performed by the Contractor during the Site Acceptance Tests (SAT), with the Employer or Employer’s representative as witness. Given that the Supplier’s responsibility ends in the on-site reception, the offloading process will be witnessed by the Contractor to check that no damage is produced during the offloading process

Robust and clearly visible signage shall be installed as is required by best practices and regulations.

## Labelling

All labels must be clear, easily visible, constructed and affixed to last and remain legible for the life of the Plant and shall, at least, report the following:

Name of manufacturer;

Product name and serial number;

Key technical parameters;

Manufacturing date and place; and

Protection index (where applicable).

Major equipment components such as PV array sections and all electric cables and circuits within the Plant shall be uniquely labelled at each end and aligned with cable and termination schedules to identify their location and function. This shall include at least the following:

PV array row numbering;

String numbering;

DC combiner box numbering;

DC/AC conversion blocks numbering;

Major components including all inverters, AC isolators, transformers, switchgears;

Mounting structure numbering;

Array tables and supporting structures;

All electrical circuits including DC string numbering, LV AC cables and HV cables, communications and signal wires; and

All required electrical safety labels and signage in line with good industry practice to identify live equipment.

Labelling and numbering systems must be aligned with Plant as-built documentation.

Any components not in compliance to the above requirements must be agreed between the Parties prior to installation.

## LV/HV Transformers

LV/HV transformers shall transform electricity from the AC output voltage of the inverters to [X]kV AC.

Step up power transformers shall be oil filled transformers from a proven manufacturer;

The transformers shall have a design life of at least 30 years;

The mouldings of the windings should contain no halogen compounds (chlorine, bromine, etc.) or other compounds capable of producing corrosive or toxic pollutants;

The oil filled transformers shall be chosen to include the following:

The insulating oil shall be free of polychlorinated biphenyl;

An environmentally preferred dielectric fluid shall be used which also maximises performance; and

A low flammability dielectric fluid shall be used.

A detection, measurement and control relay protection device is to be included within the transformers specification which will raise an alarm where the following conditions occur:

Winding temperatures;

Oil temperature; and

Small or major oil leakage and oil level monitoring.

Buchholz relay protection shall be included with accessories providing two stage protection – (i) alarm and (ii) trip;

Where necessary (concept to be agreed with the Employer), functionality will be provided for alarms to trip the HV protective switchgear to isolate the transformer. Terminal blocks for external connection of the alarm contacts shall be mounted in the low voltage compartment of the transformer;

The transformer should include but not be limited to the following accessories:

Pressure relief valve;

Oil filling point, oil draining valve and oil sampling point;

Oil level, pressure and temperature indicators (clearly visible);

Appropriate lifting lugs; and

Suitable earthing and bonding including earthing terminals.

If the site is within close proximity of a coastline or another high saline environment, the transformers will be equipped with special protection against salty air and dust to prevent reduced life time. If a breather is included, then it should have silica gel to prevent moisture ingress into the transformer tank;

The LV/HV transformers shall have a vector group according to the Employer’s design specification and/or in line with local regulations or requirements of the Connection Agreement;

The primary (HV) winding of the transformer shall have ±2 x 2.5% rated off-load tap changers;

Transformers shall have provision for installation by lifting, jacking or rolling into position;

Transformer shall be compatible with the inverters in terms of transformer low voltage level, THD and k-factor;

The transformer’s core and neutral connections should be separable through a link and should be individually accessible from outside;

Transformers shall be capable of operating in a temperature range of -25 °C to +55 °C and a relative humidity range of 5% to 95% and in the Site Conditions; and

If the transformer is to be connected to inverter by means of coupled LV busbars, then the transformer LV bushings shall support such busbar connections to provide a rigid and secure connection.

## Enclosures

Enclosures shall comply with the following minimum specifications:

Inverter enclosures shall be designed to house relevant equipment, which may include one or more inverters, a transformer and switchgear;

Enclosures shall be in the form of pre-fabricated lockable substations or in an outdoor installation protected with weather-proof material to at least IP55 protection degree for internal usage and IP66 protection degree for external usage. Enclosures shall be designed to ensure equipment within the enclosures remains functional within weather conditions at the site specified in the Contract;

Containers shall be of suitable size and weight to allow ease of delivery, installation and maintenance;

Where more than one inverter is housed in a single inverter enclosure, the inverters will be connected and protected on the AC side in a low voltage switchboard provided by the Contractor;

Satisfactory air flows should be maintained inside containers in order that there is no power de-rating in high ambient temperatures. Inverter enclosures must if necessary be fitted with heaters in order that the operational temperature ranges of the inverters are not compromised under any circumstances. If the site is within close proximity of a coastline or another high saline environment, the enclosure will be equipped with special protection against salty air and dust to prevent reduced lifetime of the enclosure or its internal components. The enclosure ventilation system should be fitted with suitable filters prevent ingress of dust/ contamination;

Cable wells are to be fully accessible for maintenance. All incoming cable ducts to the enclosure shall be filled and glands to be fitted on cable entrances to prevent any water ingress;

Enclosures will be supplied with door locks of an appropriate specification to ensure access can only be achieved by permitted individuals. All door locks must have adequate weather proofing to prevent corrosion and maintain the correct operation of the lock;

Suitable auxiliary supplies system for all the equipment in the cabin including but not limited to inverters, protections, ventilation, communication, lightning and power sockets;

Suitable earthing and bonding shall be provided;

Enclosures shall have provision for installation by lifting, jacking or rolling into position;

Enclosures shall be capable of maintaining an appropriate environmental for internal equipment in a temperature range of -25 C to +55 C and a relative humidity range of 5% to 95% and the specific Site Conditions;

The stations are to be sited in positions that ensure no shadows fall on the PV array that impact performance;

Cable wells are to be fully accessible for maintenance. All incoming cable ducts to the Power Conversion Block shall be filled and glands to be fitted on cable entrances to prevent any water ingress; and

Enclosures shall be suitably designed and raised above ground level to prevent flood damage.

Measures to prevent vermin entry shall be put in place.

## Energy Meters

Energy meters will be free issued by the Employer to be installed by the EPC/ICP Contractor. At a minimum the following requirements shall apply:

All electrical measurements shall have a range extending up to at least 120% of the maximum rating of the equipment;

To have a Class 0.2 (as per IEC 60044-1) accuracy rating,in line with local regulatory requirements; and

Check meters are to be installed, irrespective of local connection requirements.

The commissioning shall be undertaken by the Employer appointed MOP (Meter Operator Provider).

## Electrical Protection

Protection systems shall disconnect the Plant (with correct discrimination) to minimise damage from faults. Main and backup or dual protection schemes, as selected by the Contractor, shall be installed using modern protection relays.

### AC Protection and Circuits

The safety switches / circuit breakers to protect the electrical components against short circuits and overload must comply with the relevant parts of IEC 61727, IEC 60898, IEC 60715 and IEC 60947.

The electrical installation must comply with IEC 60364 and especially part 7-712 “Requirements for special installations or locations - Solar photovoltaic (PV) power supply systems”.

Circuit breakers and isolators, not fuses, shall be used for the AC main power line part of the Plant.

### HV Switchgear Units

The Contractor shall design and specify Plant switchgear to comply with all relevant regulations and design requirements as set out by the Connection Agreement and the Permits. The selected switchgear must comply with IEC 62271.

All HV switchgear will be selected with the following parameters in mind to ensure optimisation.

The primary current of the transformer;

The insulating medium of the transformer;

The position of the substation with respect to the load centre;

The kVA rating of the transformer;

The distance from switchgear to the transformer; and

The use of protection relays suitable for the purpose of the switchgear.

A sequential energisation mechanism shall be included to limit the total inrush current on energisation, as required to maintain suitable voltage levels at the connection point.

Switchgear should consist of:

One motorised circuit breaker for protection of high voltage transformers/grid;

One on-load switch disconnector per incoming feeder;

The Applicant's equipment selection and procurement process will involve specifying non-SF6 equipment with allowable exemptions only if the operating duty cannot be met or planning parameters would otherwise be exceeded;

Switchgear shall include the following characteristics;

Gas or air insulated switchgear of circuit breaker type or load-break switch suitable for purpose.

Contain all necessary relays for control of the switchgear must be state-of-the-art and comply with relevant IEC/IEEE standards;

Include metering and protection CTs and VTs;

Include interface protection with the external grid and shall also include the current protection relays (50-51, 50-51N, 67/67N, 27, 59, 81, 86);

Incorporate all necessary measuring and metering devices;

Include local current and voltage metering indicators for all switchgear units;

Earth switching;

Suitable earthing and bonding;

Include provision for providing status and live HV indication to operators;

Provision shall be provided for integrating the remote control and status indication from the circuit breaker, switches and relays to the control room through SCADA;

Switchgear should be controlled by interlocking keys where required to ensure strict compliance with correct operating/isolation sequences and enforce operating state. The interlocking mechanism shall ensure the personnel and equipment safety and include following interlocks as minimum:

between switch disconnector and earth switch;

between earth switch and circuit breaker;

across operational boundaries;

cable compartment covers (when switchgear is live); and

covers containing any live parts;

Switchgear shall provide easy access to the cable compartment for maintenance; and

Switchgear shall be capable of operating in a temperature range of -25 C to +55 C and a relative humidity range of 5% to 95% and in the Site Conditions.

### LV AC Protection and Auxiliary Services

The Plant design will include suitable provision of low voltage AC power to serve the necessary auxiliary loads, such as: power supplies for monitoring and weather systems, UPS system, if applicable, inverter ventilation fans, and fire detection and suppression system, PPC, EMS and SCADA systems, power outlets and lighting, etc. AC power may be provided from auxiliary transformers, direct low voltage connection to the grid, via string inverters, or via another methodology accepted by the Employer.

Each auxiliary transformer and distribution circuit will be sized according to the load and be protected with circuit breakers, short circuit protection and residual current devices (as necessary).

## Lightning Protection and Earthing System

### Lightning System and Overvoltage Protection

A lightning and overvoltage protection system shall be designed according to IEC 62305, all parts and country-specific regulations. The Plant shall be equipped with a lightning protection system whose LPS class should be defined by a lightning risk assessment.

The Lightning study will be conducted by the Contractor or any ICP Subcontractor who will disseminate on release. The Contractor or any ICP Subcontractor will design the appropriate Lightning protection system for the Plant, of which each Contractor will be responsible to install within their own CDM area (i.e. Contractor will install the designed protection within their area of the Plant).

The risk assessment must be undertaken to define the protection against physical damage to structures, life hazard and protection of electrical and electronic systems. The risk assessment should consider protection requirements from site mobilisation and the protection scheme to be implemented for the temporary construction compound.

The main components and systems belonging to the Plant’s lightning protection system are listed below:

External lightning system (structural lightning protection); and

Internal lightning protection (electrical and electronic system protection).

The necessity of an external lightning system shall be established in a lightning risk assessment. Where required, the external lightning system shall consist of an air termination network, down conductors and bonding connections to the earthing system, its scope is to protect the fabric of buildings and structures against lightning damage.

The internal lightning protection of the installation shall mainly consist of Surge Protection Devices (‘SPDs’) at the origin of the power and communication lines and near to the electrical components to be protected, and will be rated to ensure their protection against overvoltage as per the lightning risk assessment or the specific overvoltage protection study.

The type and characteristics of the SPDs to be installed must be in line with the lightning risk assessment or the specific overvoltage protection study. The assessment/study should specify at minimum the type, voltage protection level, maximum continuous operating voltage, nominal discharge current, insulation requirements etc. The surge protection equipment and Insulation Co-ordination Study shall ensure protection against voltage transients as well as electromagnetic interferences arising from such disturbances as switching operations, secondary induced potentials and load rejection (including islanding configuration events if applicable). Electrical precautions to eliminate the possibility of equipment acting as a source of lightning-induced transients into the grid and other Plant components shall be implemented.

### Earthing System

The earthing study will be conducted by the Contractor or any ICP Subcontractor who will disseminate on release. The Contractor or any ICP Subcontractor will design the appropriate earthing protection system for the Plant, of which each Contractor will be responsible to install within their own CDM area.

During pre-construction, an earthing study will be undertaken for the estimation of the earth potential rise expected for the Site. The earthing arrangement will be designed and installed based on the results and recommendations made in the earthing study and according to the Standards and Regulations for the Plant. Compatibility with the expectations of the study should be verified after the implementation of the earthing system.

The Contractor shall provide the complete earthing system to provide a safe Plant.

The cross-sectional area of the earthing conductors should be chosen to carry, without danger, the greatest earth fault currents and leakage currents likely to occur while having regard to thermal and electromechanical stresses.

The earthing system and its connections and components must be designed as a minimum for the Design Life to have adequate mechanical strength, protection and stability against corrosion including oxidation, formation of an electrolytic couple, electrolysis, etc.

The earthing design must respect the permissible touch voltage and permissible step voltage, transferred potentials and electromagnetic compatibility requirements according to the Applicable Standards and Regulations for the Plant. Furthermore, the earthing system shall be designed, constructed and erected to safely withstand the mechanical and thermal effects resulting from short-circuit currents.

The earthing system shall be consistent with any requirements of the Connection Agreement and will consider and be compatible with any earthing systems to be installed by the GNSP.

### Equipotential Connection

All non-current-carrying metallic components, cases and structures shall be connected to each other and to the earthing system.

Module frames shall be installed according to the manufacturer’s specifications. Whenever these require earthing of the frame, this shall be executed in compliance with the manufacturer’s specifications. Alternative solutions may be approved by the Employer and by the manufacturer. Bonding straps shall be bolted. Self-tapping screws are not acceptable.

Adequate earthing must be maintained throughout all metal work across the Plant through adequate bonding connections to the main earthing grid as per earthing design. All electrical systems and exposed metal work must be considered within the design of the earthing system and connected where required.

## Cable Selection, Design and Connections

All cables with sections or lengths exposed to Site Conditions shall be appropriately selected to be resistant the Site Conditions.

- This section includes general requirements for the cabling of the Plant. Further specific requirements for PV Facility cables selection, design and connections are specified in the respective Technology Specific ER documents.

### Cable Sizing

The cables used for wiring each section must be selected based on relevant Standards and to ensure that they can withstand the extremes of the environmental, voltage and current conditions, under which they may be expected to operate.

The cable sizing of the generation DC, HV AC, MV AC, LV AC and auxiliary supplies LV AC, shall comply with the following criteria:

Ampacity criteria: The ampacity of a cable, or current carrying capacity for continuous service, is the maximum current that can flow continuously through a cable, considering the particular method of the installation and environmental conditions, without damaging the cable's insulation and other components. The cable should be sized to withstand their ampacity for the entire lifetime of the project;

Short circuit criteria: In short circuit conditions the current flowing through the cable increases causing a temperature rise within the cable. Cables should be sized in such a way as to be able to withstand the largest possible short circuit current; and

Voltage drop criteria: the voltage drop in any circuit must respect the component specification, where component nominal voltage range specifications are not available, then the maximum voltage drop should be respected according to the applicable Standards.

The maximum current carrying capacity must be established according to best practice and the manufacturer information, always taking into account the type of cable and the installation methods. Thermal dimensioning of DC cables shall be based on heat load values evaluated in accordance with the manufacturer’s recommendations and relevant sections of BS7671:2018, IEC60228 and IEC60364 or equivalent.

All above ground cables require adequate support through the use of cable tray / basket or shall be installed so as to ensure:

Cable weight is adequately supported;

Cables conform to minimum bend radii;

Cables and connectors are not stressed or under undue tension;

Cables are protected from sharp edges;

Cables are secured so as to avoid swinging of cables due to wind; and

Cables and connectors are prevented from contacting the module back-sheets or any other object potentially causing damage to the cable or connector or the object itself.

DC String cables specifically must be protected by split ducting / kopex or gromet strips whenever coming in contact with burred edges of mounting structure. Split ducting / kopex should be used to protect the strings from direct UV wherever reasonably practicable.

The cable connectors will fulfil at least the requirements of the international protection rating IP67.

Cabling and stringing arrangements shall be in accordance with the inverter installation manual. Cabling routes should be optimised for the shortest possible distance in order to prevent additional cable losses.

The installation method chosen by the Contractor must cause no damage to cable sheaths during handling or installation and pulling forces on cables must be minimised. Minimum bending radii of cables shall be followed as per the manufacturer’s recommendations and good practice.

Underground cables must be protected from damage by termites, rats, mice, rabbits and other animals and be housed in ducts to enable easy replacement if needed during the operation of the plant.

### DC Cables

Cables used in the DC distribution network shall be especially designed for PV systems and:

Be resistant to ultraviolet radiation and ozone, with a minimum UV resistance lifetime of 20 years;

Have an enhanced resistance to heat and fire and with low smoke emissions;

Operate in an extensive temperature range compatible with site conditions;

Be rated to the appropriate DC voltage 1000V or 1500V, pending on Contractor’s design;

Be double insulated; and

Be halogen free.

Cable connectors (MC4 or equivalent) shall be IP67 rated, and at both the PV modules and String Inverters/Combiner boxes terminations shall match exactly in terms of brand and type to those on the PV modules and String Inverters/Combiner boxes. The cable connectors must on the PV module side must be supplied as a set from the Contractor, matching the cable connector to the PV module connector.

### LV AC Cables

- AC Collector cables shall comply with the Applicable Codes and Standards and be suitable for the Site conditions. They shall also meet the following requirements:

AC Collector cabling shall be copper or aluminium cables, with XLPE (cross-linked polyethylene) insulation and PVC sheath will be used for the LV installations. The Contractor shall take into account the movement of the single-axis tracker structure (if applicable) when selecting the characteristics of the conductor;

AC Collector cabling shall be specified for nature of the load and shall be rated for potential voltages that can occur on the output of the inverter;

Cables shall be ultraviolet (UV), ozone resistant and ducted where appropriate to protect against rodents;

Cables shall be sized appropriately to account for ampacity, short circuit and volt drop. Cable sizing calculations shall use appropriate soil thermal resistivity values as per site conditions for calculating direct buried or ducted cables. If direct buried cables shall be bedded in sand, this must be taken into account in cable sizing calculations

### High Voltage Cables

The cable specification must be fit for purpose and in line with the relevant Standards, codes and regulations.

In most cases HV cables shall include 3 single cores cables and an earthing conductor in twisted configuration. Each single core cable shall include:

An aluminium or copper conductor of suitable size;

Semi-conductive conductor sheathing;

XLPE insulation;

Metallic screen made of aluminium or copper strands; and

Protection against ingress of water and outer XLPE or PVC jacket.

The cables shall have the following application characteristics:

Cable for fixed installations;

Adequate for the transmission and distribution of energy in high-voltage networks. Suitable for interior, exterior and underground installations; and

Low halogen content cable with low emission of smoke and non-propagator of fire.

Cables are to meet the following Standards of manufacture or equivalent local standards where applicable:

Nominal voltages: as appropriate for the connection;

Maximum temperature of the conductor shall remain within manufacturer requirements assuming a reasonable duration of full output operation at high ambient temperature;

Maximum temperature in short circuit: 250ºC (maximum 5 s);

Curvature radius: 15 x Ø external;

Halogen-free;

Low emission of smoke; and

Non-propagator of fire.

### Communication Cables

Communication cables longer than 5 meters must be fibre-optic, rather than metallic conductors. Where this is impossible, e.g. for inclinometers, the cables must be suitably specified and designed (i.e. shielded, earthed conduits, surge protected, etc.) to prevent any harm to other components of the Plant from voltage surges or induced currents and fireproof to be used for critical safety related systems.

All communications cables shall comply with the Applicable Codes and Standards and be suitable for the site conditions. They shall also meet the following requirements:

Be durable and suitably rated against UV, anti-hydroscopic and be protected against vermin;

Be ducted where they are underground;

Cable for RS-485 shall be 24 AWG 7-strand tinned copper; 2 twisted pairs; overall foil and tinned copper braid shielding; chrome grey PVC jacket. AWM Style 2919; EIA-485; CM/CL2;

Ethernet cable shall be Cat 6a or higher, depending on the distance;

Data communications cable shall be stranded copper AWG 18-22, twisted pair, shielded Belden 1120A or equivalent;

Fibre Optic (FO) cable must be of loose tube construction and buried in trenches inside a subduct with pulling chambers if required, ideally located to allow the installation of the cable by blowing or pulling;

The subduct joints must be 100% waterproof, adapted for burial installation in high groundwater areas;

Any Manufacturer specification on the cable datasheet in relation with the implementation, such as the minimal radius of curvature, the tensile strength, or the temperature condition, etc. should be adhered to;

Each installed cable should be visibly marked at both ends.

### Auxiliary Power Cables

For the avoidance of doubt, all auxiliary power cables shall be protected by surge protection devices as per EN 61643.11 and .12 or equivalent local standard.

### Cable Runs and Trenches

In both Direct Buried or Ducted cables, a minimum of 100mm of sand all around the cable/duct is required for protection. A sand soil thermal resistivity ≤1.2Km/W must be used, and the ground conditions must be accounted for in the electrical calculations.

The technical requirements for cable runways/trenches include the specifications set out here. Local standards shall apply if more conservative or compulsory.

Buried cables within 600 mm below surface shall either be armoured or otherwise protected from mechanical damage. The Contractor shall assess the Site for potential harm from fauna and institute adequate protection measures for all cables contained within the ground.

Where cables are run within ducts or conduit, the mechanical protection must be appropriately sized to ensure thermal capacities are respected and to reduce resistive losses from the cables. The cables shall be protected from metal edges and openings. Underground cables must be protected from damage by termites, rats, mice, rabbits and other animals and be housed in ducts to enable easy replacement if needed during the operation of the plant.

The bottom of each trench shall be as level as possible and any change in gradient or level shall be made as gradually as possible. Trenches shall be free of stones and other sharp objects and the edges of the trench shall be cleared of any stones, tools or objects which may fall into the trench and damage the cable. Cables shall be covered by an appropriate material in line with their specifications and at a burial depth to be agreed with the Employer.

The communication Cables must have always at least 300mm clearance from any power cables, for avoidance of interference of the signal. If required, the contractor can supply shielded communication cables to ensure that the communication signal will not be affected.

In addition:

All ducts must be sealed with approved fire resistant expanding foam and then capped with a fire resistant, outdoor rated, UV resistant sealant.

All trenches must have cable identification marker tape placed above each cable/trefoil or duct. ideally traceable tape for comms.

cables need to be suitably protected when crossing under trafficked areas e.g. slab

Duct crush rating should be selected based on trafficked areas and expected loading.

Separation of topsoil and subsoil on excavations (not just trenching)

As built documentation, GPS routes of all cable trenches and routes

### Cable Jointing and Termination

Cable joints shall not be permitted without written approval of the Employer, any approved cable jointing necessary must be made within designated buried jointing bays or above ground jointing enclosures and clearly identified. All cable must also be adequately supported so that no weight or stress exists on the termination.

## UPS

The Contractor shall design, supply and install appropriate backup power systems and procedures to allow the Plant to maintain visibility and be able to be promptly restored to operation following an outage.

UPS’s shall have sufficient capacity to supply the required load for a period of at least 8 hours, unless otherwise required in relevant Standards. UPS protection shall be provided for:

HV switchgear;

Security system.

Weather station(s) and SCADA system; and

Inverters if required by DNO/local regulation.

## Scada System

The SCADA System will be designed and installed by the Contractor, however all installed equipment must be compatible with the chosen SCADA system should adhere to these ERs.

### Key Functionalities and Requirements

The SCADA system shall comply with, but not be limited to, the following functional specifications:

Provide real-time monitoring of the key parameters of the Plant;

Ensure data acquisition and recording for the lifetime of the Plant (historical information/archiving system) including, but not limited to, all data, events and alarms required for maintenance and operation works, as well as PV plant performance analyses. The granularity of the Data will be agreed with the Employer;

Manual and automatic control features;

Alarms generation, processing, notification, historical archiving and management system;

Automatic and manual flexible reporting features (included but not limited to daily, weekly, monthly, yearly);

User friendly and flexibly query of historical data, alarms and events;

Generate graphs for data trending analysis;

Export data, alarms and events in standard editable formats e.g. *.csv, *.xlsx.;

Share data and relevant SCADA information via APIs;

Provide concurrent local and remote access to authorised users. Local and remote access shall be done securely following all relevant guidance issued by NCSC for National Critical Infrastructure;

Web based and friendly graphical user interface, including all mentioned key functionalities and features;

Allow the integration and operation of Employer’s and third parties SCADA systems, including remote retrieval of data and certain control features (where applicable). The SCADA system shall also allow the Employer’s third-party system (such as NAME) to control all or only sections of the plants (e.g. setting different modes for the PV Plant);

Redundancy for key components, such as central server, database, power plant controller(s), internal communications backbone (fibre optic cable ring), internet access and interface to third parties (where applicable) such as Utility’s SCADA system, to prevent/minimise loss of data and communication issues;

Fibre optic cable rings shall be designed in such a way that the failure of one or more nodes will not stop data reaching the main SCADA system(s);

Use of open industry automation and communication protocols (e.g. Modbus, DNP3, IEC 60870-5, IEC 61850, OPC UA, IRIG timecode, NTP, PTP, etc.);

Use of cybersecurity mechanisms (e.g. firewalling, VPN connections) to ensure secure access and protect the system against external cyber threats. The system(s) cybersecurity setup shall be validated by a Penetration test carried out by a specialised supplier;

Support different access level depending on user roles (e.g. viewer, operator, engineer) to protect the integrity of the system and prevent unwanted, unwarranted and/or unsafe Plant configuration changes. The system(s) shall be able to log all user’s activity and changes to the system. Log shall include time stamp, unique user id, system accessed, change made showing old/new values;

Analyse SCADA system health/status, including hardware (e.g. servers, power plant controllers, etc.), software (e.g. database, Human Machine Interface, etc.), internal and external communications and interfaces; and

A local workstation, including desktop computer, keyboard and mouse, printer with a suitable number and sized screens (to be validated by the Employer) shall be provided for local access to the SCADA system by the operators of the Plant.

The SCADA system shall:

Comply with the requirements for Class A monitoring systems defined in IEC 61724-1;

Comply with the Connection Agreement, PPA, NCSC for National Critical Infrastructure and grid code;

Provide controlling capabilities of the grid parameters at the Point of Connection to meet any applicable requirements such as active power curtailment, ramp rate control, dynamic grid support such as voltage regulation, reactive power (Q) control, power factor control, Q at night, etc.;

Be designed and built for the operating lifetime of the combined PV plant;

The SCADA system and all its applications shall be provided with a permanent and comprehensive license, and therefore, there shall be no recurring fee over the lifetime of the Plant. An agreed number of user licenses shall be provided to the Employer;

Critical SCADA components shall be fed with secured power by means of an UPS properly sized to ensure a minimum operation time of 8 hours in the event of an outage in order to prevent loss of data and ensure graceful shutdown of the SCADA equipment. Critical components shall include, but not be limited to, central electronics and software, operator local workstation, all hardware related to internet access and interface to third parties and other critical field equipment such as remote terminal units, IEDs, power plant controllers and weather stations;

The key components of the SCADA system (e.g. servers, power plant controllers, remote terminal units) and monitored equipment (e.g. IEDs, energy meter, weather stations) shall be synchronised by means of a GPS based time server and industry standard network time protocol(s);

The Contractor is responsible of providing a complete, functional and comprehensive SCADA system, including but not limited to, the design, supply (all required hardware, software and wiring), installation, integration, development and commissioning of the system, full user manuals covering all functionality and monitoring of the plant(s). Manuals need to be bespoke to the installation in addition to the generic documentation issued by the manufacturers; and

All SCADA hardware and cabling shall be designed and rated to operate within the environment weather conditions applicable to the Plant. SCADA equipment shall be industrial rated with enclosures, cabinets and racks properly designed to ensure that the hardware will be operating within the temperature and humidity ranges according to the manufacturer’s recommendations.

A suitable user-focused training session shall be provided to Employer’s and O&M Contractor personnel. It shall cover all required aspects of the SCADA system from the user point of view.

### Data, Events and Alarms

Data, events and alarms will be agreed with the Employer. The following equipment shall be considered in the SCADA system design:

String boxes;

Inverters;

Grid transformers;

LV/HV transformers;

HV transformers and load tap changer - where applicable;

Capacitor banks, static synchronous compensator and/or static var compensator – where applicable;

Auxiliary transformers;

HV switchgear;

Revenue meters;

Power quality meters;

Power plant controllers;

IED;

Weather stations;

UPS system; and

Miscellaneous dependent on project such as ventilation system and temperature of critical technical rooms, substations or buildings, diesel generators, etc.

The SCADA system shall monitor the health (status) of all equipment, and generate and record alarms in the event of failures to ensure prompt remediation actions and prevent loss of data.

SCADA alarm management system shall be able to categorise alarms by severity (low, medium, high), provide real time status of alarms (e.g. timestamp active, clear, acknowledged, unacknowledged) and supporting details of the issue. SCADA signals acquisition shall comply with the sampling and recording intervals defined in IEC 61724-1 for Class A monitoring systems, and shall be able to be settable (if needed) via software to meet the Plant’s needs (e.g. 1 minute, 5 minutes, 15 minutes, 30 minutes, 60 minutes, etc.). Critical alarms shall be notified via email/SMS to ensure prompt intervention of the operators. All alarms sent by emails/SMS shall include supporting details of the issue, relevant time stamps and values/thresholds as necessary. The system shall be fully configurable and allow alerts generated for different monitored signals to be delivered to different multiple email addresses/phone numbers.

A complete SCADA signal list including monitored data, thresholds to trigger the relevant alert levels. events, alarms and calculated data shall be provided for Employer approval prior to installation of the SCADA system.

The SCADA system shall allow the user to retrieve any historical recorded data, locally and remotely, in standard editable data formats (.xlsx, .csv, .txt or equivalent and APIs).

### Data Storage

All historical data shall be available during the operational lifetime of the Plant. The Employer shall have unlimited access to the historical data. Access to this data shall be protected by the relevant cybersecurity setup and validated by Penetration Test.

All historical data shall be mirrored and stored on a secured offsite server (cloud system), to be agreed with the Employer, with a minimum storage capacity of 25 years and continuous backups to guarantee availability of all data throughout the entire lifetime of the Plant. The Employer shall have unlimited access to the data backups.

The cloud server will meet the following minimum requirements:

24/7 security guard(s);

Automatic fire suppression;

Environmental monitoring;

Video surveillance;

Alarm system;

Air-conditioning;

Generator; and

UPS (2N+1 power redundancy).

### Weather Stations

The Contractor shall design, supply, install, commission and integrate into the SCADA system the weather stations of the PV Facility.

The quantities and technical specifications of the sensors shall be in compliance with the requirements defined in IEC 61724-1 for Class A monitoring systems.

Each weather station shall be equipped, as minimum, with the following sensors:

Weather station

Global Horizontal Irradiance: 1 x digital pyranometers (Class A, IEC61724, ISO9060);

Global Inclined Irradiance: 1 x digital pyranometers (Class A, IEC61724, ISO9060), to measure the incident irradiation on the plane of the modules;

Albedometer (only for projects with bifacial modules): 2 x digital thermopile pyranometers (Class A, IEC61724, ISO9060);

1 x Ambient temperature sensor (shielded ventilated);

1 x Air humidity sensor (shielded ventilated);

3 x Module temperature sensors as minimum (final quantity according to IEC 61724-1);

1 x Air pressure sensor;

1 x Wind speed sensor;

1 x Wind direction sensor;

1 x Rain level sensor;

1 x Soiling ratio measuring station, according to IEC 61724 and including both measurement methods 1 and 2;

Lightning detection/warning system at main weather station.

Suitable solutions should be provided to measure the module temperature for projects with bifacial modules. Supplier calibration certificates shall be provided for each Individual sensor.

All sensors shall be rated for outdoor environment and shall operate within the temperature and humidity range expected for the Plant.

Each weather station shall be equipped with an industrial rated data logger with the following minimum specifications:

Enough data capacity to prevent loss of data in the event of an electrical outage or communication issues;

Shall be powered with a secured power supply system (LV auxiliary power together with an UPS system based on battery, battery charger and solar module to ensure the continuous operation of the weather station even in the event of a long-term outage);

Supporting standard industrial protocols (e.g. Modbus TCP, DNP3) for reliable communications and easy integration into the SCADA system; and

Installed in an enclosure suitable for outdoor and rated to ensure the protection of the data logger and other electronics and electrical equipment housed in it.

## Security System

Supply and installation of a site security system consisting of:

A remotely monitored CCTV system shall be provided for the surveillance of the perimeter fence and gates. Fixed position dual thermal and optical cameras built into one housing that are to be fitted to hot dipped galvanised bolt down foldable columns with predrilled holes for the mounting of the cameras and Power supplies. The columns will elevate at 3 metres, subject to planning conditions above ground level, positioned ideally 1 metre in from the perimeter fence. The cameras and poles will be installed in a clockwise rotation with each camera providing protection to the next camera in line with a maximum distance of 65 metres between columns. The camera systems shall be digital based systems which shall be user configurable, scalable, utilize digital storage devices and be connected to the monitoring facilities via a local area network. This system will also include an onsite audio challenge facility.

The Contractor shall be responsible for the design and positioning of CCTV cameras at strategic locations, mounted on buildings or using masts as required in the planning conditions, to achieve the full coverage of the perimeter fence and gates. Where the conditions do not state these requirements, the Contractor shall design the system considering long-range fixed position infrared cameras fitted to poles which will elevate at 3 metres above ground level and positioned 1 metre in from the perimeter fence. Each pole will be fitted with a camera providing adequate coverage with a tilt down function to alleviate any need for working at height to carry out any maintenance tasks. So that each camera provides protection to the next camera in line with a maximum distance of 65 metres between columns, depending on topography. The use of concrete shall be minimised for the installation of posts, ducts or draw pit cable boxes.

The overall design of the CCTV system shall be such that images of the subject of interest are captured, displayed and stored with sufficient resolution to enable a positive identification at any position within the area of coverage. The CCTV images displayed on the monitors shall be of adequate clarity to provide clear and unambiguous identification of persons or motor vehicles. Solid state CCTV cameras utilizing charge coupled devices (CCD) capable of providing high-definition colour video images shall be provided. Cameras installed in areas which are likely to be subject to changing light levels shall have lenses equipped with auto iris control facilities.

Infra-red lighting shall be provided for cameras where the level of illumination during the hours of darkness is insufficient to give a clear image. The beam width of the lighting shall be matched to the focal length and coverage of the camera. Infra-red lighting shall be switched automatically by photocells during the hours of darkness.

A digital storage system shall be provided capable of storing the CCTV images in time lapse or in real time modes as required. The images shall normally be stored in time lapse mode. The storage system shall have facilities to superimpose camera number and date/time data on the images.

The cameras shall be networked together using a dedicated local area network with sufficient segments to optimise the cabling requirements without compromising the system performance and throughput. The network cabling shall be tamper-proof.

Remote monitoring provisions in accordance with the latest General Data Protection Regulation (GDPR).

Should a security breach arise such that the CCTV becomes operational, the UPS should be capable of running for at least 6 hours.

CCTV cameras shall be located at all access points to provide clear identification of people and motor vehicles. The access control system is to include the provision of an audio challenge facility and can provide key holder response.

Keypads will be fitted to gated access points agreed with the Client.

### Fence and Gate

Before the commencement of the works at Site, the Plant area shall be secured by installing appropriate fencing.

The final fencing design (including gates for access) shall be approved by the Employer, prior to installation.

A guidance of the fence line and type of fence required has been included in the approved planning documentation. Please refer to these documents for detailed information.

### Security During the Construction Phase

During any period when the Site is unmanned, a contracted security company is to monitor the Site on a continuous basis and conduct periodic patrols. If any suspected theft is noticed this is to be immediately reported to the local police and the Employer. The security company must be able to prove that they have adhered to their walk around every hour and as such a method of evidencing their work is needed.

The security company is to be paid for by the Contractor as part of the scope of works.

### Permanent Security Arrangements

The Contractor shall provide an integrated and complete operational security system for the Plant. Intruder detection and surveillance equipment shall be provided for the Site to deter unauthorized access to the Site while permitting ease of access to authorized staff and visitors.

All security measures shall be fully integrated to allow an automatic response to events to aid operator decisions.

The Plant is to be protected from both casual and malicious intrusion.

The security system shall have at minimum the following equipment and systems installed:

Perimeter security fence and motorised gates;

Security system to be designed and installed by NSI Gold certified installer;

Continuous CCTV coverage of the entire perimeter fence and key internal areas including (but not limited to) the O&M building, the workshop and stores, the substation and the main gate;

CCTV cameras must have minimum Lux response and be supplemented with infrared illuminators if necessary to maintain visuals throughout the night. Night vision resolution shall be sufficient to allow footage to be used by the Police for identification purposes;

CCTV cameras shall have a minimum optical resolution of 1920x1080 and minimum infrared resolution of 640x480;

CCTV cameras shall have a minimum bitrate of 4mbps per camera;

CCTV cameras shall record at a minimum of 25fps per channel;

CCTV cameras placement shall meet minimum requirements for NSI approved ARC to respond alarms;

Audio challenge shall be fitted in key areas (e.g. main gate and container areas);

Spares containers shall be locked using locks minimum specifications, with doors to be alarmed and CCTV cameras fitted to inside of containers;

A motion detection system and infra-red (thermal) detection system should be incorporated;

All cameras must link to a local central station and there should also be a link to a remote server for back-up;

The cameras shall have a minimum recording time of 10hrs per day of at least 30 days;

Intruder detection to buildings; and

The surveillance and alarm system shall communicate with the central alarm system, which should also communicate with the system SCADA system.

Forced intrusions shall be detected by the automatic surveillance and alarm system. The alarm must be able to alert a remote central security location and an appointed representative of the Employer.

All security measures shall be fully integrated to allow an automatic response to events to aid operator decisions. It is the responsibility of the Contractor to ensure that the security systems comply with local regulations.

## Lighting

Sufficient lighting shall be provided to comply with good practice. External security and general external site lighting to building areas including inverter stations and primary access point shall be provided by the Contractor for operation and security during construction.

During Construction, if any additional lighting is required for night-time construction, this is to be provided by the Contractor, compliant with the below listed conditions.

Building perimeter lighting shall be controlled via photo-electric cells and the Site lighting shall be switched in circuits by means of externally mounted weatherproof switches.

Energy efficient lighting shall be used as far as reasonably practicable.

In any case, the Contractor shall:

Minimise the off-site lighting impacts;

Ensure that all external lighting associated with the Plant;

Is installed as low intensity lighting (except where required for safety or emergency purposes);

Does not shine above the horizontal; and

Complies with relevant local standards associated with the effects of outdoor lighting and planning requirements of lighting.

## Temporary Site Facilities

All work on Site shall be carried out in an orderly and workmanlike manner and shall present a neat appearance in accordance with good industry standards and practice.

The Contractor shall keep the construction site clean and tidy in order to facilitate construction work, to avoid damaging the equipment intended for the Works and to reduce the likelihood of fires occurring and injury to workers.

The Contractor shall supply, erect, maintain any and all temporary structures such as:

Site offices for Employer and Employer appointed 3rd parties;

Site offices for the Contractor’s own staff and sub-contractors staff; and

Storage sheds, workshops, tool sheds and employees' amenities sheds, change room, toilets, catering and canteen area and sanitary accommodation, etc.

that are required for the execution of the Works.

Specifically, before the start of construction or compatibly with the presence of labour at Site, the Contractor shall procure to have on Site and in appropriate locations the following facilities:

Table 5: Site description

| Facilities | Notes |
| --- | --- |
| Facilities for the Employer | - As per section 9.13.1 |
| Changing facilities |  |
| Sanitary facilities |  |
| Potable water facilities |  |
| Canteen or similar space |  |
| Sewage and wastewater facility |  |
| First aid room |  |
| Site manager’s office |  |
| Security office |  |
| Wheel washing facilities at the entrance of the site for trucks and cars |  |
| Storage container for minor parts | - These can be located elsewhere for convenience |
| Car parks |  |
| Loading / unloading and storage area |  |
| Security arrangements |  |

The sizing of the facilities and amenities provided shall take account of the projected manpower levels.

The Contractor shall provide all surface preparation required and shall supply, install and maintain water supply and drainage systems and a general electrical supply system.

If required, the Contractor shall be responsible for arranging housing at his own expense for construction workers at a suitable location. The housing facilities shall be sufficient to allow the workers good quality rest and sleep.

All facilities shall be regularly and systematically maintained and cleaned to ensure safe, proper and efficient operation at the responsibility and cost of the Contractor.

On completion of the Works, the Contractor shall remove from site all temporary structures and services including sanitary arrangements and shall rehabilitate all parts of the Site impacted by the Contractor’s temporary structures and services.

### Facilities for The Employer

The Contractor shall provide temporary Site office solely for the use of the Employer and the Employer’s personnel. These offices shall be provided at the same time as the Contractor mobilises to Site.

The Employer’s site office shall be complete with furnishings which shall include 1 desk with chairs, filing cabinets and air conditioning. Facilities such as photocopier, telephones, high-speed internet service (as per Section 2.2), shelving, toilet facilities, kitchen facilities must be provided but may be shared with the Contractor’s personnel.

All facilities shall be regularly and systematically maintained and cleaned to ensure safe, proper and efficient operation at the responsibility and cost of the Contractor.

On completion of the Works, the Contractor shall remove from site all temporary structures and services including sanitary arrangements and shall rehabilitate all parts of the Site impacted by the Contractor’s temporary structures and services.

# Transport, Testing and Commissioning

Plant specific requirements for commissioning and testing, over and above any requirements contained in the Section 12 (which must be adhered to) are described within the Technology Specific ERs and below.

The Contractor shall notify the Employer of the date, time and location of all tests a minimum of 10 business days prior to the commencement associated test, unless otherwise stated. The Employer may witness some or all of these tests or may nominate a representative to witness the testing.

## Transport and Arrival to Site

The Contractor shall comprehensively document all transportation and site arrival tests and inspections necessary to ensure quality of the Works.

## Mechanical Completion

Prior to Mechanical Completion of the Plant, the Contractor shall perform an in-situ visual inspection on all components of the Plant:

The component is free of visible damages that might affect the safety of the component and of the personnel;

The component has been installed properly;

The usage of materials and proper installations adequate with the environment in which the component is installed;

The component is readily accessible for the operations set out in the O&M Contract;

The electrical installation has been performed according to the Contract and the Contractor’s design documentation;

The component has been installed according to the prescriptions imposed by the manufacturer;

The readiness of the installation and of the calibration of all protection and signalling equipment forming part of the Plant, including Plant documentation and equipment documentation, equipment labelling;

The availability of electrical drawings, safety manuals and usage hand books;

The identification and correct labelling of fuses, breakers, circuits, etc. as well as all major items (modules, inverters, transformers, etc.);

The proper labelling of cables and boards;

The proper execution of the connections, demonstrated by cable point-to-point testing where applicable;

The component has been installed according to the prescriptions imposed by the manufacturer;

The existence of the necessary protections against electrical shocks due to active parts insulation damage (indirect contact);

The existence of factory tests reports or quality test reports from manufacturer, when applicable; and

The provision of a certificate from the Contractor confirming that the Works have been constructed in accordance with Applicable Law.

Visual checks are applicable on all the components that form part of the Plant, including the Grid Connection Works and fitting systems. The following parts as a minimum shall be subject to visual inspection:

Inverters;

Foundations;

Mounting structure;

Photovoltaic modules and DC installation;

Mains, pits, cabling, electrical boxes and protection devices;

Internal connections and interconnections with external installations;

Monitoring system including any UPS;

Low voltage installation, including protection equipment and utility interconnection equipment;

High voltage installation, including transformation, protections equipment and utility interconnection equipment;

Grid Connection Works;

Security system;

Grid connection line and fitting systems;

Equipment labelling in agreement with plans; and

Health and safety signage.

Moreover, the visual inspection shall verify the installation of system components complies with the design. This shall include a review of the following:

Labels and markings;

Safety signs;

Rated power of components;

Number of components;

Distances, heights and positions of components and systems;

Size of cables, wires, busbars;

Module flash tests;

Tightening torque of bolts;

Cabling paths and cable arrangements, with particular focus on the string cables; and

Alignment of PV tables.

To achieve Mechanical Completion of the Plant, the correct positioning of the system components must be verified, in particular:

Coordinates of structures, cabins, fence, power stations and cable paths;

Compliance of the Works with the [insert applicable permit for development] and the constraints applicable to the Site area in terms of position of the equipment, occupation of the areas, compliance with the prescribed Site borders;

The correct orientation and inclination of the photovoltaic modules; and

The presence of safety signs at the prescribed locations.

#### Civil Works

To verify the installation of civil works meets the design compliance the Contractor shall:

Verify the roads are in accordance to the design requirements and are in good condition;

Verify there is no erosion and that all slopes, drains and soils have been stabilised to prevent erosion in the design life;

Verify the drainage has been executed to design;

Verify that fencing has been completed as per design;

Verify that hedgerow remediation has been completed where necessary;

Verify temporary sediment control devices have been removed;

Verify that any concrete work has been completed as per the design. In particular, the following should be checked:

Geometries of foundations are as per design;

Concrete cover is as per design and no exposed rebars appear;

Concrete works shows no cracks; and

Concrete samples for foundations and footings have been collected and tested as per the applicable standards and results made available.

Concrete:

Concrete samples for foundations and footings shall be collected and tested as per the applicable standards and results made available as part of the Mechanical Completion requirements.

Steel:

Structural steel and rebar steel samples shall be collected and tested as per the applicable standards and results made available as part of the Mechanical Completion requirements.

The Contractor shall provide a test report outlining the test methodology and evidence demonstrating compliance with test acceptance criteria. The Contractor shall include all test records and certifications.

#### Verification of Foundations

This test shall be applied to all foundations including PV mounting structures/trackers and is required for Mechanical Completion.

The test shall commence after complete installation of all mounting structures/trackers and all PV modules and earthing connections to the PV array. The Contractor shall:

Perform pile-out tests, concrete compressive strength tests or any other required tests to satisfy the designer of the foundations;

Provide test records and/or installation records to demonstrate the installation meets the design;

Compaction/subgrade testing of subgrade or structural fill materials if used;

Visually inspect the foundations and piles to verify correct installation including verticality and alignment;

Verify the correct torquing of fasteners on structures on a random 1-2% sample;

Verify the correct material of fasteners for corrosion; and

Visually inspect the mounting structures/trackers for corrosion or damage to galvanising.

The test will be passed when all test procedures have been passed, recorded and any rectification works have been conducted.

#### Verification of Underground Cabling

This test applies to all underground cabling in the Plant including communications cable. The Contractor shall verify:

Geometric cable layout by observing and measuring of open trenches;

Mechanical protection and warning tapes;

Back fill material; and

Correct labelling.

- The test will be passed when all test procedures have been passed, recorded and any rectification works have been conducted. The Contractor shall provide a test report outlining the test methodology and evidence demonstrating compliance with test acceptance criteria including photographic record of the complete installed length prior to backfill.

#### Verification of The Combiner Boxes/ String Inverters

With respect to mechanical completion tests for combiner boxes/string inverters. the Contractor shall perform and record:

Visual inspection of the combiner box;

proper sealing;

no condensation or dirt ingress; and

connections are securely tightened.

Verify integrity of surge protection devices and all earthing connections;

Inspect the condition of each combiner box;

Verify minimum height above ground level is complied with;

Verify it is properly sealed;

Verify all cables and conductors are correctly terminated and connected;

Verify all labels are installed as per design and requirements;

Verify there has not been any water ingress through any of the joints, check there is no condensation;

Verify there are no loose covers or poorly fastened elements that could allow water or dust to enter;

Verify the enclosure is not damaged and that it is securely installed and fastened;

Verify that the cabling is properly supported and protected; and

Verify all cables have been tested as per the testing protocol, including but not limited to, insulation resistance, polarity check, cable continuity, open circuit voltage.

The test will be passed when all above procedures have been passed, and any rectifications works have been conducted. The Contractor shall provide a test report outlining test methodology and evidence demonstrating compliance and test criteria.

#### Verification of DC Cabling

With respect to mechanical completion tests for DC wiring, the Contractor shall:

measure insulation resistance;

verify the polarity and voltage of each pair of conductors at the combiner box and inverter;

perform continuity tests;

verify cable identification/labelling is in place and correct;

verify condition of cable;

verify cables are landed and lugs are torqued to appropriate value in accordance with manufacturer's data;

verify that all cabling is installed as per design;

verify that all the cables are fastened at regular intervals and that no sharp edges may affect the cables; and

verify that all cable transitions (e.g., above ground to below ground, etc.) are appropriately fastened using weather resistant jointing elements.

The test will be passed when all above procedures have been passed and any rectifications works have been conducted. The Contractor shall provide a test report outlining test methodology and evidence demonstrating compliance and test criteria.

#### HV Cable Insulation Testing

The HV Cables will be checked visually during installation and Insulation Resistance (IR) testing will also be performed prior to and after the backfill of the cable trench. Visual checks, IR/VLF/IR testing of the conductor core to screen and screen to sheath will be performed once terminations have been completed. The HV cables will be tested with a 5kV IR verification test prior to energising.

The Contractor shall megger the cable screen to earth to check for resistance of the jacket shielding and insulation to check there are no defects in the cable insulation and that the values in all sections are below the limits in the applicable standards.

If the test determines a section is not in good condition and does not comply with the requirements of the EPC Contract the Contractor shall perform all remedies required to solve the problem and repeat the test to verify the problem has been corrected.

The Contractor shall deliver all megger certificates with the control sheet signed by at least two authorized personnel of the company responsible for performing the test. The Contractor shall provide a test report.

#### Protection Relay Tests

The protection relays and associated switchgear shall be fully installed.

The following inspection and testing will be performed but not limited to:

Visual inspection of protection panel and labelling according to design drawings;

Tightness test of all connection;

Detailed inspection of LV wiring;

Dielectric tests on auxiliary and control circuits;

Inspection and testing of earthing, including VT circuits;

Functional testing of all mechanical and electrical switches, lockout switches testing facilities; and

Functional testing on lockout, padlocking facilities.

Tests should include verification of the functionality of the protection relays, including by primary injection and secondary injection. The protection study and settings shall have been accepted by the NSP and network operator for implementation.

#### Switchgear and HV Switchboards

The following inspection and testing will be performed but not limited to:

Visual inspection of switchgear and labelling;

Check clearances;

Tightness test;

Detailed inspection of LV wiring;

Dielectric tests on auxiliary and control circuits;

Inspection and testing of earthing;

Functional testing of all mechanical and electrical interlocks;

Functional testing on padlocking systems;

Functional testing of circuit breakers and auto-reclose;

Verification of CT and VT ratio to design through available certificate polarity and earthing;

Test anti-condensation heater operation;

Busbar Ductor Resistance; and

Busbar Hi-Pot.

#### Power Transformer LV/HV

The following inspection and testing will be performed but not limited to:

Visual inspection of all transformer and labelling;

Oil level and pressure;

Tightness test;

Detailed inspection of LV wiring;

Dielectric tests on auxiliary and control circuits;

Inspection and testing of earthing; and

Functional testing on padlocking systems.

#### Earthing System Test

Ensure that all components are properly and firmly earthed in compliance with the Standards and Applicable Law. Welding and bolt tightening shall be verified.

The Earthing system shall be inspected and tested in accordance with the Standards. Tests should include:

Visual inspection of key components and joints;

Continuity and loop resistance testing; and

Current injection testing.

These tests shall only be undertaken when the earthing system is completely installed. It should also be performed for relevant sections of the site prior to energising any portion of the works that require the earthing system to be functioning for safe operation.

Point to Point Earth Continuity testing is performed between the HV main earth bar, HV Switchboard and metallic structures as required by the earthing design.

The Contractor shall:

Perform a visual inspection of all accessible earth cabling and check the condition of the cables and conductors;

Verify all elements, including all cable tray sections if applicable, are connected to the earthing system by a fastener, terminal or by electrical continuity of the structure; and

Measure earthing resistance of 50% PV array earthing and 100% of all other earthing systems forming the Plant.

The Contractor shall provide a test report outlining test methodology (Slope fall of potential method or similar if more appropriate) and evidence demonstrating compliance to standards (EN50522) and to design (target earth resistance value achieved) and test criteria.

#### HV Circuit Breaker

The testing shall include but not be limited to:

Visually inspect the HV circuit breaker and labelling;

Inspect and test the earthing;

Interlocks;

SF6 pressure and quantity (if applicable);

Heater check;

Spring base torque; and

Functional test.

#### HV Line Isolator and Earth Switch

The testing shall include but not be limited to:

Application checks; and

Visual inspection.

#### HV Voltage Transformer

The testing shall include but not be limited to:

Application checks;

Visual inspection;

Verify product matches specification;

Verity product installed as per design; and

FAT test certificate available.

#### HV Current Transformer

The testing shall include but not be limited to:

Application checks;

Visual inspection;

Verify product matches specification;

Verity product installed as per design; and

FAT test certificate available.

#### Auxiliary Transformer and LV Distribution Board (AC & DC)

The testing shall include but not be limited to:

Visual Inspection of transformer and labelling;

Visual inspection of circuit breakers and labelling;

Inspection and testing of earthing; and

Connections are secure and tight.

## Punch List

The Contractor shall maintain a comprehensive punch list identifying any issues which must be addressed with respect to the Plant. The punch list shall be managed according to the following punch list priority levels:

Type A: items to be mitigated/addressed and closed in order to achieve the Mechanical Completion;

Type B: items that are not considered as a stop-point for safe energisation and which are however to be mitigated/addressed and closed as a condition for issuance of the Completion Certificate; and

Type C: minor items not considered as a stop-point for safe operation of the Site, but which have to be mitigated/addressed and closed within a fixed timeframe to be agreed between the Contractor and the Employer.

## Energisation Tests

The Energisation Tests shall consist of:

Pre-commissioning tests; and

Commissioning tests.

A detail description of each energisation test is included in the following sections of this ERs. All parts of each of the Energisation Tests must be successfully completed to the Employer’s satisfaction and shall be in compliance with the IEC 62446.

The following procedures shall be complied with by all parties during the conduct of the tests. Any modification to these procedures shall require the Employer’s prior approval and be treated as a variation to the Contract.

Energisation Tests shall be executed only once the Contractor has submitted the notification of readiness to commence the Energisation Tests and the Site can be considered substantially complete.

### General Requirements

The Contractor shall take responsibility for and perform all test and commissioning activities necessary to enable connection of the Works to the Grid and to demonstrate the safe operation of the plant in accordance with the requirements of the Contract. The tests shall confirm the readiness of the Works to operate in compliance with requirements of all relevant Laws, regulations, and requirements of the Connection Agreement, allowing export of 100% rated capacity of the Works to the Grid.

### Test Protocol

The Contractor shall submit to the Employer a test protocol summarising the Pre-Commissioning Tests and Commissioning Tests in a form substantially satisfactory to the Employer (the ‘Test Protocol’). The protocol shall be agreed between the Employer and Contractor before commencement of the tests. The Contractor or any ICP Subcontractor will also require sight and input so as to coordinate all necessary tests into the grid connection and internal RMU commissioning schedules.

The Contractor shall submit its proposed Test Protocol to the Employer for review and approval not later than thirty (30) Business Days prior to the scheduled commencement of any Tests. The Contractor’s Test Protocol shall summarise the pre-commissioning tests and commissioning tests in a form substantially satisfactory to the Employer comply with and detail all requirements contained in the Contract and include sample Test Result submissions.

The Employer shall review the Contractor's proposed Test Protocol and provide comments to the Contractor within ten (10) Business Days after receiving it from the Contractor. Approval by the Employer shall not excuse the Contractor from its responsibility to conduct testing and commissioning activities in accordance with the Contract.

The basic content of the Test Protocol shall include, but not be limited to, the following:

Outcomes of the inspection of the Work;

Methodologies for the tests;

Instrumentation used for the tests;

Periods of execution of the tests;

Conditions under which the tests have been carried out;

Test Data;

Results of the functional tests;

Results of the functional tests at the substation;

Results of all the tests requested under the PPA (if any) to be executed at this stage;

Results of all the other tests;

Commissioning protocols released for the key components (inverters, transformers, etc.);

Results of the continuity tests, isolation tests, ground resistance tests, cable tests;

Summary of the results; and

Confirmation that the Plant has successfully completed the Tests.

### Data to be Provided by Contractor

The Contractor shall provide the Test Data for all Tests in the format agreed within the Test Protocol to be compliant with the model reports specified in IEC 62446 as well as auditable electronic format.

### Certification by Contractor of Test Results

The Contractor shall certify to the Employer in writing that the Test Results and supporting data provided by the Contractor are complete, current and accurate.

The minimum required information for testing (following IEC 62446) shall be documented in the ITP.

## Pre-Commissioning Tests

The pre-commissioning test scope shall include but is not limited to the functional test defined in IEC 62446 Grid connected photovoltaic systems – Minimum requirements for system documentation, commissioning tests and inspection and the electrical testing requirements of AS3000. The minimum scope of the pre-commissioning tests is described in detail below.

### Name Plate Capacity Test

The Contractor shall demonstrate that the installed capacity of the Works meets or exceeds the Name Plate Capacity. The installed capacity shall be calculated by summing the module flash Test Data for all modules installed as part of the Works.

### Functional Tests

The Plant shall be subject to a functional test which should include confirmation that components operate within the expected parameters as well as respond correctly to transient conditions.

The test will include the Functional Test under IEC 62446.

As part of this set of functional tests the following shall be completed.

#### Switchgear

Contractor shall review factory test documentation to confirm that all LV, MV and HV switchgears have passed all factory tests, including

Type test;

Functional tests;

Contact resistance;

Insulation resistance; and

Other tests applicable to MV and HV equipment, such as high-voltage withstand, earth switch resistance, air pressure / vacuum / SF6 leakage tests (as applicable).

All switchgear (LV, MV and HV) shall be tested according to manufacture manual and applicable Standards. The following test shall be performed by the contractor:

All circuit breakers shall be tested according to manufacture manual and applicable Standards;

Operation of circuit breakers including verification of rated operated sequence, operation timing, coil & contact resistance, insulation resistance, contact voltage withstand test, and power factor;

Verification of anti-pumping functionality;

Operation of isolator and earth switches including open/close and spring recharge;

Functional tests of operation counters and position indicators;

Functional tests of control and indication circuits in local and remote modes;

All protective relays shall be tested according to manufacture manual and applicable Standards;

Protection relay programming;

CT insulation resistance test;

CT ratio check;

CT magnetising test;

VT insulation resistance test;

VT polarity check;

VT ratio check;

Primary and secondary injection testing of protection;

Busbar Ductor Resistance;

Busbar Hi-Pot;

Verification of correct phase rotation;

Functional testing of OLTC Controller operation; (by others); and

All surge arrestors shall be tested according to manufacture manual and applicable Standards.

#### Transformers

All LV/HV transformers shall be tested as per IEC 60076 [and AS2067] after installation and prior to energisation, including

Visual inspections;

All LV/HV transformers shall undergo an oil sampling campaign after installation and prior to energisation. Oil shall be tested by a third party and shall show conformance with the applicable limits in terms of moisture, particles and gas content;

Voltage ratio test;

DC-winding resistance test;

Leakage reactance (impedance) test;

Insulation resistance test

Torque checks;

Earthing checks;

Thermal trip checks;

Correct settings for tap;

All requirements as detailed by the manufacturer's instructions;

Check clearances;

Verify transformer against name plate and tap position;

Check of mechanical connections including all earth connections;

Check tap selector switch operation and position;

Check all auxiliary contacts for correct operation and are correctly set;

Check oil level and temperature;

Check correct signage and labelling; and

Check to ensure no air in transformer relays.

#### CT and VT

In addition to Visual inspection the following test shall be performed on CTs and VTs.

Insulation resistance;

Polarity check;

Ratio check;

Burden and volt drop;

Winding resistance;

Winding resistance;

In-service check;

Magnetising;

Primary injection;

Helmet connection; and

Accuracy.

#### Line Disconnector and Earth Switch

All switchgear (LV and HV) shall be tested according to manufacture manual and applicable Standards. The following test shall be performed by the contractor:

Insulation resistance;

Contact resistance; and

Aux contact timing.

#### Auxiliary Transformers and Distribution Boards

The tests will include:

a visual field inspection;

confirmation of Ratio;

PI;

Insulation and winding resistance;

Vector group test;

Voltage ratio test;

Positive seq impedance test;

Current Transformers and Voltage Transformers;

testing for all metering devices permanently connected

Meters:

Auxiliary meters should be installed, commissioned and signed off by Network operator.

Polarity of all circuits shall be verified against the design drawings;

All low voltage switches shall be tested according to manufacture manual and Applicable Standards; and

Verify that switches used in DC applications are rated and installed accordingly.

#### Telecom and Scada System

All Fibre optic cables shall be tested for continuity of signal and signal loss.

The contractor shall perform End to end testing for all control and monitoring function:

All control functions shall be tested and verified as operable; and

All alarms shall be verified tested and verified as operable.

#### Cables and Busbars

All low-voltage DC and AC cables shall be tested for insulation resistance in accordance with IEC 60364-6, IEC 60364-7 and other Applicable Standards. All faulty sections have been identified, replaced and re-tested;

All connection bolts for busbars and cable terminals should be marked have their torque checked;

All low voltage cables shall be inspected and tested in accordance with IEC 60364-6, IEC 60364-7 and other applicable Standards. The Employer will require a witnessed installation test report and a certificate of compliance test report; and

All high voltage cables shall be tested for insulation resistance in accordance with IEC 60502-2, IEC 60840 and other Applicable Standards.

All high voltage connections shall be tested for conductivity and contact resistance (e.g. ductor testing).

## Commissioning Tests

Commissioning is a systematic process of ensuring that the systems perform according to the design intent and the future operational requirements. All equipment and systems should be installed, assembled and tested according to manufacturer’s recommendations and the best practices and standards of the industry.

The commissioning process involves:

Integration of each sub-system to work with its interfacing sub-systems;

Testing of each sub-system and then the complete system to demonstrate that they meet their requirements; and

Commissioning of each system together with the systems of others where they interface so as to bring the system whole into operation.

The commissioning tests are performed to determine and verify the proper operation of the System Plant and all its sub-system components.

Commissioning tests shall include, but not be limited to, the following sub-system and systems:

PV Modules;

Inverter;

Auxiliary systems;

Power transformer;

Switchgear;

SCADA system;

Security system;

High-voltage substation system;

Extra High-voltage substation system; and

Grid Connection system of Others.

The commissioning works will be carried out in phases:

Phase 1, Mechanical completion as minimum the following test shall be completed

Factory acceptance tests 2.24.1;

Installation release tests 10.2;

Phase 2, Pre-commissioning test 10.5; and

Phase 3, Energisation and commissioning.

Each phase will produce test datasheets and reports which will be made available to the next phase in order to minimise re-testing. All the test listed into this section shall be performed by the contractor which can optimise the logic and the sequence of the testing.

All the tests shall be listed on the test schedule, included in the inspection and test plan (section 5.2). The Employer must be made aware when the test will happen and has the right to witness the test.

The Equipment shall be tested at Site. These tests shall prove whether the equipment meets the requirements and the safety conditions, whether it has been built and/or erected with satisfactory workmanship and whether the equipment is in conformity with the prevailing standards and regulations, the manufacturer's recommendations and installation/ commissioning procedures and with the present state of modern technology.

The Technology Specific ERs hold more details for specific tests . Please refer to these documents for completeness.

### Transformer Commissioning

Power transformers (LV/HV transformers) shall be commissioned by an authorized representative of the manufacturer using the manufacturer’s specified procedures.

Commissioning reports shall be issued in a format provided by the manufacturer.

The commissioner shall execute at least the following tests and checks:

Visual inspection. Check mechanical state and earth connections;

Check correct earthing;

Check tightening torque of bolted connections;

Insulation check (with measurement of insulation resistance) (primary to secondary – primary to earth – secondary to earth);

Measurement of turns ratio and vector group;

Measurement of no-load losses and current;

Measurement of short circuit impedance and load losses;

Measure insulation resistance between all windings and each winding to earth;

Measure insulation resistance core-to-earth;

Check transformer polarity and phase relationship;

Positive sequence impedance test;

Magnetisation test;

Bushing test (tan delta);

Sweep frequency response analysis;

AC voltage withstand test;

Test on on-load tap changer;

Check tap selector switch in correct position;

Check oil leakages (for oil transformers);

Check oil level (for oil transformers);

Check overpressure valve (for oil transformers);

Check of protection devices;

Check of alarms (oil level, Bucholz, temperature);

Check saturation of dehumidifying salt;

Dielectric test (for oil transformers);

Functional tests of tap changer, interlocks, temperature relays and other auxiliary equipment;

Noise level test;

No-load test (when applicable);

Check satisfactory equipment labelling and warning;

Oil sample tests including breakdown strength, moisture content and dissolved-gas content;

Test inert gas pressure system where applicable;

Check all control, fans and pump for correct operation;

Wiring checks including Control cabling checks;

Buchholz test;

OLTC surge relay test (if relevant);

Pressure relief valve test;

Neutral earthing check;

Tap change local operation (TCD);

Tap change limit switch check; and

Manual crank check;

All tests shall be executed according to IEC 60076, IEC 60270, IEC 60156 and all other applicable Standards to be detailed by the Contractor.

### Scada System Functional Test

All SCADA system equipment shall be commissioned and tested using the manufacturer's specified procedures.

Tests shall verify the correct operation of the SCADA system, meters, sensors, weather station instruments, and all inverters, while verifying the correct data input logging from trackers (if trackers are used as the mounting structure), breakers, and other components monitored by the system.

The SCADA system shall be fully accessible remotely and should adhere to strict cybersecurity requirements, including:

IEC 62443; and

Employer’s cybersecurity and IT requirements.

This test shall verify that the data collected is correctly received by the SCADA System and can be used to produce any required performance or operation reports. Each row of data shall report the exact date and time in a suitable format. Testing shall include but not be limited to:

Verify that all required data is able to be received, recorded and displayed correctly by the SCADA system. Every tag will be verified for appropriate reading and scaling;

Verify that all data exchanged with external systems is correct in both directions;

Verify correct polarity of all generation data;

Verify that all events are received and logged at the SCADA system;

Verify self-healing ring topology by checking individual ring segments by isolating each from the rest. The test will ensure that the communications network correctly re-configures when fibres are disconnected;

Verify connectivity with individual plant elements through connection of a PC to local plant network;

Verify all communication systems, modems, routers etc.;

Verify all SCADA software, users accounts and cloud systems;

Verify all SCADA alarms notification (email, SMS);

Verify all SCADA backup systems;

Verify all communications system in the office/control room;

Verify all third parties SCADA control/measuring systems;

Ensure correct data acquisition from all devices to be monitored;

Demonstrate 99% reliability over a continuous period of 240 hours;

Verify local and remote access;

Demonstrate correct behaviour of alarm system and actions including remote alerts and alarms;

Control of a group of inverters and individual inverters;

Demonstrate proper functioning of the metering devices;

Calculation of availability and performance ratio in accordance to the EPC Contract; and

The Contractor shall specifically check all control settings are in accordance with the requirements of the Network Service Provide and the EPC Contract.

A SCADA system commissioning protocol or report shall be provided. Contractor to supply a complete list of every HMI tag, control function and I/O with Principal, NSP and AEMO confirming correct reading, date of check and name of checker. 100% of data points shall be field verified.

### Security System Functional Test

Security system equipment shall be commissioned, tested and calibrated by a certified installer of the equipment manufacturer using the manufacturer’s specified procedures.

The Contractor shall be responsible for these tests but shall be assisted by any ICP Subcontractor wherever necessary.

Security system testing shall include testing of all operating modes and alarm conditions, including testing of:

Cameras and dome cameras;

Image analyser;

Infrared sensors / projectors;

infrared barriers, microphone cables, microwave barriers (if any), audio challenge.

Lights;

Sirens;

Reaction time of security company;

Verification that the installation is in accordance to the design and EPC contract;

Visually inspect the entire perimeter is fenced and that there are no gaps that could compromise security; and

Verify all gates can be opened from the inside without a key for emergency exit

A security system commissioning protocol or report shall be provided.

### Weather Station

To commission the weather stations the Contractor shall:

Verify all weather station equipment includes up to date calibration certificate;

Verify that equipment is not obstructed by any object including a check that there are no shadows or reflection on pyranometers;

Verify validity of data collected and check to ensure there are no erroneous values or discrepancies. Compare results of different weather stations and ensure correct alignment of all irradiance sensors by verifying there is no crossing of irradiance curves. Check magnitude of measured values for sensors in the same plane have a sufficiently small error;

Verify correct attachment of all temperature sensors;

Verify that the PV modules used for the soiling stations have the same features and specifications of the PV modules in the project;

Verify the data is properly received, displayed and recorded by the SCADA system; and

Verify operation of back-up power supply.

A test report shall be provided.

### Buildings

The Contractor shall:

Provide a certificate of classification for all buildings and structures classified as buildings;

Verify all spare parts can be housed inside the warehouse and can be readily accessed; and

Verify all requirements of the EPC contract have been met including verification of telecommunications facilities required under the EPC Contract are installed and functioning correctly.

### Fire and Smoke Detection Systems

All fire indication panels and smoke detectors are to be tested. All associated SCADA alarms to undergo a functional test. The fire and smoke detection systems to be commissioned in accordance with the manufacturer’s specifications and [AS1670].

The test will be passed when all above procedures have been passed. The Contractor shall provide a test report including raw data from the SCADA system demonstrating correct operation and communication of all fire and smoke alarms.

### High-Voltage Substation Commissioning

The Contractor shall liaise with the DNO in order to determine the necessary compliance requirements for testing and commissioning. Not less than three (3) months in advance of the commencement of the commissioning tests the Contractor must advise the DNO, of the Test Protocol including test procedures and test equipment to be utilised during the commissioning tests. Should the DNO require that changes be made to the Test Protocol the Contractor shall implement the changes without delay and resubmit.

The Employer shall be included in all communication and invited to participate in all meetings held with the DNO.

The Contractor shall proceed with the commissioning of the substation as agreed with the DNO and in line with the relevant Law and Standards.

Before energisation, the Contractor shall verify completeness of the substation and correct installation of all the components. A detailed inspection of the substation shall be carried out. A check list shall be handed over to the Employer for approval forty (40) days before completion of the Works and this shall be used during the final inspection.

Following the inspection, a set of tests shall be executed which shall include, but not be limited to, the following:

Commissioning of all the structures, supports, foundations, buildings as required by applicable Law and Standards;

Commissioning of components and systems as described in Technology Specific Sections;

Tests that confirm communication capabilities for remote monitoring, operation and protection systems of the Works by the Contractor, and the facilities for the Works to receive and respond to instructions for semi-scheduled operation received by DNO.

### Commissioning of Components and Systems

All tests prescribed by the manufacturers shall be executed in accordance with the prescriptions contained in the respective installation and commissioning manuals. The following list of tests shall be complied with whenever manufacturers’ tests are less restrictive than the detail presented here.

HV circuit breakers

Check earthing;

Completeness of installation and cleanliness of insulators;

SF6 pressure;

Functional tests;

Tests for verifying opening / closing time;

Measurement of power absorption of the coils; and

Measurement of resistance of the main contacts.

Current transformers

Check earthing;

Completeness of installation and cleanliness of insulators;

Check versus SF6 pressure or oil level;

Check connections;

Check ratios and data sheet parameters;

Turn ratio test; and

Verification by injection of current to the primary.

Voltage transformers

Check earthing;

Check tightening of bolts;

Completeness of installation and cleanliness of insulators;

Oil level; and

Check ratios and data sheet parameters.

HV disconnectors

Check earthing;

Check tightening of bolts;

Completeness of installation and cleanliness of insulators;

Verify greasing of main contacts and moving parts;

Check setting of limit switches;

Check interlocking between earthing and disconnector;

Perform electrical manoeuvres;

Perform mechanical manoeuvres;

Functional tests; and

Measure resistance of main contacts.

Surge dischargers

Check earthing of supports;

Check earthing of dischargers;

Check earthing of counter;

Check tightening of bolts;

Completeness of installation and cleanliness of insulators;

Measure insulation resistance;

Register number of dischargers recorded by the counter before activation; and

Measure residual resistance before activation.

Transformer

Follow procedure in 10.6.1.

HV cables

Check clamping;

Check correct positioning and orientation of toroids;

Check earthing of shields; and

Dielectric test.

HV switchgear

Check correct mounting and fixing;

Check correct earthing;

Verify correct setting of protections;

Functional tests;

Check SF6 gas pressure and humidity level;

Measure insulation resistance; and

Perform dielectric tests.

Auxiliary transformers

Follow procedure in 10.6.1.

AC and DC panels

Check correct mounting and fixing;

Check correct earthing;

Verify correct protection settings; and

Functional tests.

Protection devices

Check correct mounting and fixing;

Check correct earthing;

Check feeding voltage;

Verify correctness of settings;

Functional tests; and

Check tripping of protections by injecting current.

Fire alarm, lighting system, Diesel generator, and other systems

Check correct mounting and fixing;

Check correct earthing;

Verify correct setting of protections; and

Functional tests.

- Meters

Verify proper wiring and installation;

Verify proper current and voltage transformer specifications based on required accuracy classification;

Verify proper CT & VT ratio programming into meter;

Verify meter is accurately capturing and recording performance data;

Compliance with [network operator/AEMO] requirements; and

Verify remote access to meter reading and that high-speed data is sufficient for [GPS/grid] compliance monitoring can be accessed and downloaded remotely.

#### Thermography of Electrical Connection

This test will be undertaken when the Plant is operational and there are stable irradiance conditions with a minimum irradiance of 600W/m2 for global horizontal irradiance. This procedure shall be performed for all:

Combiner boxes;

Transformers;

Inverters;

Switchboards;

Distribution boards; and

Accessible electrical connections.

The Contractor shall:

a) Verify the connection are properly connected;

b) Verify the metal masses are properly connected to earth; and

c) Take a thermal image to verify the proper condition of connections and to detect hot spots.

If there is a temperature difference of 5°C, particularly in electrical connections, the Contractor shall report and investigate hotspots and:

Temperatures not within the range provided by the Original Equipment Manufacturer;

Temperature differences greater than 3⁰C between similar components in the same enclosure; and

Temperature differences greater than 15⁰C between components and the ambient air.

If the difference exceeds this threshold, maintenance should be scheduled.

## Performance Tests

### Introduction

The Testing Schedules include the methodology for the following Performance Tests as part of the acceptance procedure:

Initial Performance Test (as set out in Technology Specific ERs;

Interim Performance Test (as set out in the PV Technology Specific ERs; and

Final Performance Test (as set out in the PV Technology Specific ERs.

The proposed methodology combines current market standard approaches and international best practices for the comparison of Plant performance against contractual performance guarantees. This document sets out the procedures and requirements for conducting the Performance Tests, including the process for determining Test Results and criteria for successful completion.

This methodology shall be agreed by the Parties prior to the Performance Tests commencement and followed by the parties during the conduct of the Performance Tests. Any modification to these procedures shall require the Employer’s prior approval.

### Tests and Acceptance

Notification of the Tests Commencement Date

Not later than ten (10) Business Days prior to commencing any of the Performance Tests, the Contractor shall notify the Employer in writing of the specific date and time for commencement.

If the Contractor fails to provide any of the required notices within the agreed time, commencement of the corresponding test shall be deferred until the required notice periods are met or the Employer, in its sole discretion, approves commencement of the subject test.

Conduct of the Tests

The following procedures shall be followed by all parties during the conduct of the tests. Any modification of these procedures shall require the Employer's prior written approval.

The Employer and the Contractor shall each appoint a test representative, who will be responsible for representing their respective companies during the conduct of the tests.

During the conduct of the Performance Tests, all incidents shall be recorded in the test log book.

Plant Operation During the Tests

During the conduct of the Performance Tests, the Contractor shall be responsible for the operation of the Plant in compliance with the O&M Contract including, but not limited to, maintenance and sensors and equipment calibrations, cleaning of sensors, cleaning of the Modules, detection and resolution of PV plant issues, including monitoring data quality.

Data to be Provided by Contractor

The Contractor shall provide the Test Data and Test Result for all Performance Tests in the auditable electronic format agreed by parties.

Certification by Contractor of Test Results

The Contractor shall certify in writing to the Employer that the Test Results and supporting Test Data provided by the Contractor are complete, current and accurate.

Acceptance or Rejection by Principal of Test Results

Within fifteen (15) Business Days following receipt of all required Test Results, supporting Test Data and Contractor's certification of the Test Results, the Employer shall notify the Contractor in writing that the Test Results submitted by the Contractor are either accepted, rejected or incomplete. If the Test Results are rejected, the Employer shall provide the basis for rejection. If the Test Results are incomplete, the Employer shall identify the missing information. Within ten (10) Business Days following full submission of the missing information by the Contractor, the Employer shall notify the Contractor in writing whether the Test Results are accepted or rejected.

Repeat Of Performance Tests

If the Employer rejects Test Results for the Initial Performance Test submitted by the Contractor, the Contractor shall undertake again the applicable test in accordance with these Testing Schedules and all applicable Contract requirements.

Dispute Resolution

If the Contractor disputes the Employer's rejection of any Test Results or if the Parties disagree on any of the Test Results the Parties shall follow the disputes resolution procedures set forth in the Contract.

Safety During Testing

The Contractor shall be responsible for safely conducting all Tests. The Contractor shall provide a safety briefing for all personnel on the Site who will be involved in or witnessing any Tests, and shall ensure that such personnel comply with all applicable safety procedures at all times during the performance of the Tests.

### Measurement Requirements

Documentation

The monitoring system documentation (equipment and functional specifications, user guides, calibration certificates and maintenance track records) shall be provided to the Employer for review prior to the commencement of the Tests.

Sampling And Recording Intervals

For all measured parameters required for the Performance Tests, the monitoring system shall comply with the following data acquisition requirements:

Maximum sampling interval: 3 seconds;

Maximum recording interval: 1 minute; and

Test Data Point Interval: 15 minutes.

For the purpose of the Performance Tests, the Test Data Point Interval shall be 15 minutes. For each Test Data Point Interval, a 15-min data point shall be calculated as the mean value of all 1-minute records corresponding to the Test Data Point Interval.

Figure 1: Sampling, recording and Test Data Point intervals

Timestamps

Each 15-min Test Data Point Interval shall include a timestamp with the date (day, month, year) and time (hour, minute) corresponding to the beginning of the 15-min data point interval.

The time should refer either to local standard time (not daylight savings time) or universal time (UTC), to avoid winter / summertime changes.

Midnight shall be treated as the start of a new day (first 15-min data point of the day) and expressed as 00:00. The last 15-min data point of each day shall be at timestamp 23:45.

When multiple data acquisition units are involved that each independently applies timestamps, the clocks of the units shall be synchronized, preferably by an automated mechanism such as global positioning system (GPS) or network time protocol (NTP).

# Form of Progress Reports

The monthly progress report shall be provided in electronic format (.pdf or similar) and shall contain at least the following:

Plant reference;

Date;

Report progress number;

Brief summary;

SHEQ risks identified, incidents and near misses;

Environmental events (including near-misses) and issues;

Major activities executed in the month;

Major activities planned for the following weeks;

Project risks and mitigating actions implemented;

Opportunities for reduced construction time;

Record of milestones claimed and status of payment (including variations);

Forecast of upcoming milestone completion dates

Resource levels assigned to activities (including person-power allocated);

Significant existing and anticipated problems / issues / challenges with discussion of potential resolution and/or mitigation;

Visits from third-parties (e.g. fire service, LPA etc.);

Progress of:

Engineering / design;

Procurement and material delivery on site;

Construction;

After construction services (testing, commissioning, etc.);

Deliveries to site; and

Grid Connection Works (Employer’s side).

The progress shall be identified with percentages of completion for each of the sub-tasks (i.e. electrical design 50%, civil works design – foundations 80%, etc.). Moreover, progress shall be represented as follows:

Current progress against Schedule (e.g. Gantt chart);

S-curve (budget and work completion);

Critical path activities and reserves;

Milestone completion;

Third party approvals or statements required and actual progress; and

Variation order requests (indicating variation, order request status, extra costs, impact on Schedule, mitigants).

QA/QC facts, including:

Factory inspections and outcomes;

Material acceptance at Site;

Completeness of documentation;

Post-installation Test Results;

NCRs

Status of permits, licenses and authorisations to be obtained, including any changes; and

Photographic report (photos of main components and photos of works).

The weekly progress report shall be provided in electronic format (.pdf or similar) and shall contain at least the following:

Summary of activities completed this week;

Summary of activities expected to complete over the next 2 weeks;

Site weather conditions;

Onsite resources (staffing and equipment);

SHEQ incidents and near misses;

Environmental incidents or near misses;

Local community incidents or issues;

Major activities executed in the week;

Major activities planned for the following week;

General progress against Schedule;

Project risks and mitigating actions implemented;

Opportunities for reduced construction time;

Engineering documentation status;

Resource plan and allocation of personnel;

Plant planned vs. actual % complete;

Record of achieved milestones;

Forecast of upcoming milestone completion dates;

Significant existing and anticipated problems / issues / challenges with discussion of potential resolution and/or mitigation;

Problems / issues / challenges specifically affecting progress; and

Photographic report.

# Codes and Standard

Contractor shall perform the Work and deliver the Work in accordance with the Codes and Standards set forth in this section and in compliance with all other parts of the Contract.

The applicable regulations, standards and laws which are mentioned within this document, are to be regarded as non-exhaustive and do not relieve the Contractor from its obligation to provide complete and fully functional systems and facilities. The Contractor shall observe all the applicable laws, national and international standards which are relevant for completion of its Work under the Contract.

When a specific topic is not regulated by a national law or standard, the Work shall comply with the standards issued by the following organisations, in order of precedence:

Association national standards, for example:

BSI: British Standards Institution;

UBC/IBC: Universal/International Building Code;

International standards:

IEC: International Electrotechnical Commission;

UL: Underwriters Laboratories;

ISO: International Organisation for Standardisation; and

IEEE: Institute of Electrical and Electronic Engineers.

In the absence of any relevant association national standards or international standards, EN European Standards shall be used.

- Specific PV standards affecting to the components of each Facility are described in detail in the respective Technology Specific ERs.

## Statutory Regulations / Requirements

All parts of the Contractor’s responsibilities including but not limited to design, management, installation, procurement and component supply, testing and commissioning must comply with the following non-exhaustive list of statutory requirements:

Connection and Use of System Code (CUSC);

BS7671, IEC 60364, Low voltage electrical installations and HV systems;

Health and Safety at Work act 1974;

Management of Health and Safety at Work Regulations;

Environmental Protection Act 1990;

Distribution Code;

Building codes such as BS 5950 structural design;

BS 9999: Fire Safety in the Design, Management, and Use of Buildings;

The Environment Act 2021, covering waterways and environmental impacts of construction and waste management;

National Building Codes and Construction regulations, including CDM;

National Fire Prevention regulations;

Products certifications according to the national and international standards made by independent accredited laboratories; and

All relevant standards referred to in this document and appendices.

## General Standards

ISO 9001:2015, Quality management;

ISO 14001:2015, Environmental management; and

OHSAS 18001:2007 Occupational Health and Safety Management or ISO 45001: 2018.

### Power Transformers

IEC 60076, Power transformers (parts as relevant);

IEC 61378-1:2011, Converter transformers - Transformers for industrial applications;

IEC 61099, Insulating liquids - Specifications for unused synthetic organic esters for electrical purposes;

IEC 60296:2012, Fluids for electrotechnical applications - Unused mineral insulating oils for transformers and switchgear;

IEC 60422: 2013, Mineral insulating oils in electrical equipment - Supervision and maintenance guidance;

IEC 60599:2015, Mineral oil-filled electrical equipment in service – Guidance on the interpretation of dissolved and free gases analysis;

IEC 60270, High-voltage test techniques - Partial discharge measurements; and

IEC 60156, Insulating liquids - Determination of the breakdown voltage at power frequency - Test method.

## Electrical Equipment

### Overhead Power Lines

The design and construction shall be carried out in compliance with the applicable Standards, including, but not limited to, the following which, for avoidance of doubt, shall be superseded by the requirements of the DNO where applicable:

EN 50341 (all parts), Overhead electrical lines exceeding AC 1 KV;

IEC 60826:2017, Design criteria of overhead transmission lines;

IEC 60038:2009, IEC standard voltages;

IEC 60652:2002, Loading tests on overhead line structures;

IEC 60060:2018 SER, High-voltage test techniques – ALL PARTS;

IEC 60071:2018 SER, Insulation coordination – ALL PARTS;

IEC 61773:1996, Overhead lines - Testing of foundations for structures;

IEC TS 61774:1997, Overhead lines - Meteorological data for assessing climatic loads;

IEC 61854:1998, Overhead lines - Requirements and tests for spacers;

IEC 61284:1997, Overhead lines - Requirements and tests for fittings;

IEC 61865:2001, Overhead lines - Calculation of the electrical component of distance between live parts and obstacles - Method of calculation;

IEC 61897:1998, Overhead lines - Requirements and tests for Stockbridge type aeolian vibration dampers;

IEC TR 61597:1995, Overhead electrical conductors - Calculation methods for stranded bare conductors;

IEC 61395:1998, Overhead electrical conductors - Creep test procedures for stranded conductors;

IEC 61089:1991, Round wire concentric lay overhead electrical stranded conductors;

IEC 60305:1995, Insulators for overhead lines with a nominal voltage above 1000 V - Ceramic or glass insulator units for AC systems - Characteristics of insulator units of the cap and pin type;

IEC 60383 (all parts), Insulators for overhead lines with a nominal voltage above 1000 V;

IEC 60433:1998, Insulators for overhead lines with a nominal voltage above 1000 V - Ceramic insulators for AC systems - Characteristics of insulator units of the long rod type;

IEC 60720:1981, Characteristics of line post insulators;

IEC TS 60815 (part 2 or 3 as relevant), Selection and dimensioning of high-voltage insulators intended for use in polluted conditions; and

IEC 61109:2008, Insulators for overhead lines - Composite suspension and tension insulators for AC systems with a nominal voltage greater than 1 000 V - Definitions, test methods and acceptance criteria.

### General

IEC 61869, Instrument Transformers (parts as relevant);

IEC 60287-1, Electric cables - Calculation of the current rating;

IEC 60228:2004, Conductors of insulated cables;

IEC 60332-1-2:2004, Tests on electric and optical fibre cables under fire conditions - Part 1-2: Test for vertical flame propagation for a single insulated wire or cable - Procedure for 1 kW pre-mixed flame;

IEC 61034 (all parts), Measurement of smoke density of cables burning under defined conditions;

IEC 60068-2-78:2012, Environmental testing – Part 2-78: Tests. Test Cab: Damp heat, steady state;

IEC 60754-1:2011, Test on gases evolved during combustion of materials from cables - Part 1: Determination of the halogen acid gas content;

IEC 60811-100:2012, Electric and optical fibre cables - Test methods for non-metallic materials - Part 100: General;

IEC 62444:2010, Cable Glands for electrical installations; and

IEC 60216-1:2013, Electrical insulating materials - Thermal endurance properties - Part 1: Ageing procedures and evaluation of test results.

### Low Voltage

BS7671:2018;

IEC 60364 (all parts), Low-Voltage electrical installations (for topics not included in National Electrical Standards);

IEC62446: Photovoltaic (PV) systems – Requirements for testing, documentation and maintenance;

IEC 61439 (all parts), Low-voltage switchgear and control gear assemblies;

IEC 60947, Low-voltage switchgear and control gear (parts as relevant);

IEC 60269 (all parts), Low-voltage fuses;

IEC 60227 (all parts) Polyvinyl chloride insulated cables of rated voltages up to and including 450/750V;

IEC 60245 (all parts), Rubber insulated cables - Rated voltages up to and including 450/750V;

IEC 62852:2014, Connectors for photovoltaic systems. Safety requirements and tests;

IEC 60189-1:2018, Low frequency cables and wires with PVC insulation and PVC sheath – Part 1: General test and measuring methods;

TUV 2 Pfg 1169 08.2007 – Requirements for cables for use in photovoltaic-systems;

IEC 60898-1:2015, Electrical accessories - Circuit-breakers for overcurrent protection for household and similar installations - Part 1: Circuit-breakers for AC operation; and

IEC 60715:2017 Dimensions of low-voltage switchgear and control gear. Standardized mounting on rails for mechanical support of electrical devices in switchgear and control gear installations.

### High Voltage

IEC 62271, High-voltage switchgear and control gear (parts below as relevant);

-1, Common specifications for alternating current switchgear and control gear;

-100, Alternating current circuit-breakers;

-110, Inductive load switching;

-200, AC metal-enclosed switchgear and controlgear for rated voltages above 1 kV and up to and including 52 kV;

-202, High-voltage/ low-voltage prefabricated substation;

IEC 60502:2018 SER Power cables with extruded insulation and their accessories for rated voltages from 1 kV (Um = 1,2 kV) up to 30 kV (Um = 36 kV) – ALL PARTS;

IEC 62271-204:2011, High-voltage switchgear and controlgear - Part 204: Rigid gas-insulated transmission lines for rated voltage above 52 kV;

IEC 60840:2011, Power cables with extruded insulation and their accessories for rated voltages above 30kV;

IEC 60183:2015, Guidance for the selection of high-voltage A.C. cable systems; and

IEC 60840:2011, Power cables with extruded insulation and their accessories for rated voltage above 30kV (Um=36kV) up to 150kV (Um=170kV) – Test methods and requirements.

### Cable Containment, Trenches and Ducting

IEC 60364-5 (all sections), Selection and erection of electrical equipment;

IEC 61386-24:2004, Conduit systems for cable management - Part 24: Particular requirements - Conduit systems buried underground;

IEC 61386-21:2002, Conduit systems for cable management - Part 21: Particular requirements - Rigid conduit systems; and

IEC 61084:2017 (all parts), Cable trunking and ducting systems for electrical installations.

### Cable Jointing and Terminations

IEC 61442:2005 Test methods for accessories for power cables;

EN 61238-1:2003 Compression and mechanical connectors for power cables;

IEC 61914:2015 Cable cleats for electrical installations;

IEC 60947-7-2:2009  Low voltage switchgear and control gear – part 7-2: Ancillary equipment –Protective conductor terminal block for copper conductors; and

IEC 60502 Power cables with extruded insulation and their accessories for rated voltages from 1 kV (Um = 1,2 kV) up to 30 kV (Um = 36 kV).

## Security System

IEC 62676-4:2014, Video surveillance systems for use in security applications. Application guidelines; and

IEC 60839 (all parts), Alarm and electronic security systems.

## Monitoring System

ISO 9060:1990 Solar energy - Specification and classification of instruments for measuring hemispherical solar and direct solar radiation;

IEC 61853-1:2011, Photovoltaic (PV) module performance testing and energy rating - Part 1: Irradiance and temperature performance measurements and power rating

IEC 61724-1:2017, Photovoltaic system performance – Monitoring;

IEC 61850 (all parts) - Communication networks and systems for power utility automation;

IEC 60870-6-503:2014, Telecontrol equipment and systems - Part 6-503: Telecontrol protocols compatible with ISO standards and ITU-T recommendations - TASE.2 Services and protocol;

IEC 61000-6-1:2016, Electromagnetic compatibility (EMC) - Part 6-1: Generic standards - Immunity for residential, commercial and light-industrial environments;

IEC 61158 (all parts), Industrial communication networks – Fieldbus specifications;

ISO/IEC 11801, Information technology – Generic cabling for customer premises;

IEC 61784 (all parts), Industrial communication networks – Profiles;

IEC 61918:2018, Industrial communication networks – Installation of communication networks in industrial premises;

IEC 81346 (all parts), Industrial systems, installations and equipment and industrial products - Structuring principles and reference designations;

IEC 60870-5:2018 SER, Telecontrol equipment and systems - Part 5: Transmission protocols - ALL PARTS; and

IEC 62443, Industrial Automation and Control Systems Security.

## Metering

National Metering regulations;

IEC 62052 (all parts), Electricity metering equipment (AC) - General requirements, tests and test conditions.

## Mechanical, Civil and Structural Design Standards

National Building Code and Construction regulations;

IEC 60826:2003 Design criteria of overhead transmission lines;

IEC 61773:1996 Overhead lines – testing of foundations for structures; and

IEC 60364-7-704:2005 Low-voltage electrical installations: Construction and demolition sit installations.

# Project Specific Contractor Documents

This section contains a non-exhaustive list of Contractor documents which shall be provided during the Contract and execution of the Works.

Up to date printed copies of all documents, drawings and contract documents including permits and licenses shall be kept at the Contractor’s office at the Site, available for use at all times.

The Contractor shall maintain a record of all field deviations from the design drawings and shall submit to the Employer a set of Contractor’s Documents in line with the terms prescribed in the Contract.

Documents submitted should be in both native format (e.g. .dwg, .docx, .xlsx etc.) and PDF. The language of all documentation should be English.

Contractor’s Documents include the following:

General documents;

As-built and design documents;

Surveys and studies;

O&M manuals;

Installation manuals;

Specifications and data sheets;

Training material; and

Other documents.

All Contractor’s Documents shall be submitted to the Employer for comment. For the avoidance of doubt this section is not an exhaustive list of documentation, and any other documents mentioned in the Contract or identified by the Contractor as necessary to complete its scope of work must be identified by the Contract and submitted to the Employer for comment.

## General Documents

The following general documents shall be submitted by the Contractor:

Exhaustive list of codes and standards which shall apply to the Work;

Traffic Management Plan;

Project Management Plan;

Module handling plan;

Health and Safety Plan;

Quality Plan;

Environmental Plan;

Emergency response plan;

Social responsibility plan;

Interface management plan; and

Licence and permitting compliance matrix.

## As-Built and Design Documents

As-built documents shall be in accordance with IEC 62446 and should include, but not be limited to:

Site plan;

Piling depth records and plan;

Foundation plans;

Foundation design calculations;

Structural design calculations;

Geotechnical report;

Topographic survey;

Drainage system design and calculations;

Site surveys including as-build electrical equipment elevations;

Single line diagrams;

Electrical plan diagram;

Electrical cable and conduit lists;

Electrical conduit, earthing and lightning protection system drawings;

Earthing designs and layout drawings;

Final project specifications;

Design studies and evaluations;

Detailed design drawings of all components installed/works completed;

Instrument calibration certificates;

Equipment drawings;

Schematic diagrams;

Wiring diagrams;

System descriptions;

Calibration certificates;

SCADA as-built design package;

Data sheets and specifications of each component;

Complete component warranty certificates; and

Bill of materials.

Where applicable, as-built documents should include the design documents listed in Table 6 and be provided in both a native format (DWG, Word, Excel, etc.) and PDF.

Table 6: Design and as-built documentation list

DESIGN AND AS-BUILT DOCUMENTATION LIST

ELECTRICAL

Documentation

Technical description of the electrical design

Electrical calculation (including all DC, AC, LV, AC, MV, earthing system and ancillary services calculations)

Power quality study

Electrical studies including but not limited to load flow, short circuit, switching transient, transformer inrush, transient stability and dynamic performance, transient overpower, harmonic analysis, voltage fluctuation, voltage flicker, unbalanced network conditions, and power factor.

Protection studies

Energy production forecast

PVsyst simulation sheets (or alternative simulation software reports)

Electrical loss calculations

Lightning risk assessment and lightning system calculations

Grid integration study as per Grid Code and guidelines

Bill of Quantities

Drawings

As Built Trench Layout

General single-line diagram (SLD)

HV single line diagram

DC and AC single line diagram

Interconnection Plant SLD

Design of Interconnection Facility

Detailed string connection plan and string path

Earthing system layout

Earthing system – details

Lightning system (if any)

Electrical drawing of string combiner / junction box

Electrical drawing of inverter and transformer cabins

Auxiliary services SLD

Layout of cabling (AC)

Layout of cabling (HV)

Layout of cabling (communication)

Layout of cabling (auxiliary services)

Drawing of UPS and / or Diesel generator

IFC and As Built trenches and crossings

Fibre-optic cabling from PV Facility to Interconnection Point

Layouts of O&M building and substation including overall layout, equipment locations, wiring, ducting.

Specifications

PV panel

Inverter

Inverter cabin

HV transformer

HV switchgear

LV cabinets

EMS

Auxiliary transformers

Combiner boxes

Cables (DC, AC-LV, MV, communication, earthing cords, other)

Junction box, combiner box

UPS

Diesel generator

Cabin ventilation

Protection system (pilot protection, over current, short circuit, earth leakage, and any other required protection systems)

Transformer protection system

Metering system

Power quality analyser

Other

HV SUBSTATION

Documentation

Technical description of the design (architectural, electrical, mechanical, electromechanical, etc.)

Structural calculation based on prescribed local conditions (dead, wind, seismic, snow loading) for civil works, foundations, footings, Buildings

List of protection settings

Bill of Quantities

Drawings

Single line diagram (general)

Single line diagram (operating)

Single line diagram (protection and metering)

Single line diagram (communication and SCADA)

Single line diagram (AC and DC systems)

Substation layout (general arrangement)

Substation layout (elevations)

Earthing system layout

Feeders panel equipment layout

Transformer panel equipment layout

Transformer wiring scheme

Transformer protection and control wiring scheme

Bus zone and bus section equipment layout

Bus zone and bus section wiring scheme

Bus zone panel connection diagram

Lightning system (if any)

Auxiliary service wiring scheme

Generator equipment and layout

Generator equipment wiring scheme

SCADA RTU equipment layout

SCADA RTU connection diagrams

Site layout

Site contour plan

Site roads and earthworks cross sections and details

Foundations

Building architectural design

Building electrical services

Building mechanical services

Building cable tray

Building conduit layout

Building earthing

Structures of HV equipment supports

Footings of HV equipment supports

Building earthing

Fire and security scheme and equipment layout

Specifications

HV/MV transformer

Auxiliary transformers

MV switchgears

Surge arrestors

Cable potheads

Supports and bars for HV equipment

Lightning mast

Cable terminations

HV disconnectors

HV circuit breakers

Current transformers

Voltage transformers

insulators

Reactive power compensators (if any)

SCADA system components

Diesel generator

HVAC system

Meters

Fire alarms

Alarms

Power quality analyser

All other components in the Building

CIVIL WORKS

Documentation

Technical description of the civil works, including foundations, earth movements, levelling, geotechnical characteristics

Structural calculation based on prescribed local conditions (dead, wind, seismic, snow loading) for cabins and trackers/mounting structures.

Tracker/Mounting structure supplier comment on foundation design

Description of the drainage system design

Hydrological calculation report

Bill of quantities (foundations, earth works, roads, drainage system)

Drawings

General PV system layout

Grading details and slopes

Ground movement

Aerial view

Topographic elevation

Design of PV system access

Layout of roads, tracks and storage areas

Cross sections of roads, tracks and storage areas

Drainage system layout and coordinates

Drainage system channel details and cross profiles

Drainage system culverts details and cross profiles

Trenches – details

Trenches – layout

Manhole – details

Manhole – layout

Water supply system (fresh and sewage water)

Fresh and sewage water tanks design and supporting infrastructures

Cabin foundation – design

Cabin foundation – details

Tracker foundation design

O&M building and substation civil design

Tracker upper structure design

Toilet facilities

Specifications

Construction material (gravel, geotextile, concrete, crushed stone, sand, iron bars)

Electric ducts

Drain pipes

Manholes

Water tanks (fresh and sewage)

Construction facilities (WC, changing rooms, …)

Other

SCADA SYSTEM

Documentation

Technical description of the SCADA system (civil infrastructures and network)

Technical description and specification of the Communication system to be installed on Delivery Point according to Connection Agreement and/or PPA (if any) requirements

Technical description and specification of the communication network between Facility and Point of Connection including equipment, infrastructure, cabling among other required elements;

Documentation regarding configuration, parameters and programming on installed communication system

SCADA development and integration information, including configuration files of the system, SCADA hardware and field devices settings, source codes, software, credentials, licenses and any other applicable related set-up data

User manual and guides

Drawings

SCADA system block diagram (system architecture)

Layout of SCADA system (including location of string monitors, AMR, weather stations, cabinets, server and control rooms)

Full SCADA alarm code list

Communication cabling paths (optic-fibre or similar)

Fibre-optic patch plan

Typical trenches for communication cables

Single-line diagram auxiliary services

Control cabinet – cabling details

Monitoring system – cabling details

Control cabinet – details (incl. foundations)

Meteorological station layout and installation details

Specifications

AMR interfaces, weather station equipment, meters

Keyboard, computer, monitor, server, UPS

Data communication interfaces (routers, antennas, …)

Combiner boxes/string inverters

AC Isolator

Junction boxes

String monitoring unit

Cables (fibre optic, RS485, RS232, …)

Ethernet switches

Power quality analyser

Meteorological station components (pyranometer, temperature sensors, pressure sensors, humidity sensors, wind vane, anemometers, tower)

Other

SECURITY SYSTEM

Documentation

Technical description of the security system (civil infrastructures and network)

Technical description of the fence design

Manuals of each component

Bill of Quantities

Drawings

Security and surveillance system block diagram

Layout of security system (including location of pylons, cabinets, fence)

Communication cabling paths (optic-fibre or similar)

Typical trenches for communication cables

Single-line diagram auxiliary services

CCTV pylons – details (incl. foundations)

Fence – details (incl. foundations)

Gate – details (incl. foundations)

Fence layout with coordinates

Security cabinet – details

Security cabinet – foundations

Security cabinet – cabling details

Specifications

Thermal camera

Keyboard, computer, monitor, server

Illuminator (IR)

Video encoder

Cables (fibre optic, RS485, RS232, …)

Ethernet switches

Other

## Operation and Maintenance Manuals

O&M manuals shall include the following:

Plant O&M manual (general). This must include as a minimum:

Description of the Plant and the substation;

Project information including contact details of the Employer, Contractor, NSP and responsible parties;

Operating philosophy and all operating procedures;

Maintenance requirements and procedures;

Scheduled maintenance plan;

Equipment information including datasheets, list of major equipment, equipment description;

Description of SCADA system and project specific user guide; and

Overview of alarms and trips, information on settings.

Plant substation OEM O&M manuals package;

Module OEM installation and maintenance manuals;

Inverter OEM O&M manual;

Isolator OEM O&M manual

Transformer OEM O&M manual;

Tracker and mounting structure OEM maintenance manual;

Switchgear OEM maintenance manual;

Combiner box OEM manuals;

Weather station OEM manuals;

Operating procedures, local and remote. Including:

Pre-start checks;

Auto/manual start-up/energisation of plant or sections/feeders; and

Auto/manual shutdown/isolation of plant or sections/feeders.

Procedures for verifying correct system operation;

Procedure to be followed in case of a system failure or in response to an alarm;

Emergency procedures including emergency shutdown/isolation and start-up/energisation procedures;

Maintenance and cleaning recommendations;

Replacement of large equipment strategy, including placements of cranes if required;

Health, safety and environment manual;

SCADA O&M manual;

Warranty documentation;

Scheduled maintenance procedures;

Trouble-shooting procedures;

Risk assessment section and health and safety section;

Reference to As-Built documentation; and

Specialist tools list.

## Other Documents

Other Documents shall include the following:

Spare Parts list;

Lists and specifications for materials and accessories;

Flash test reports for each single module;

Manufacturer’s warranty certificates;

Quality assurance testing reports on the modules;

Quality assurance testing reports on the inverters;

Quality assurance testing reports on the transformers;

Quality and test report for the rest of the materials and equipment (QA/QC);

Earthing protection drawings and survey reports;

Site electrical test reports;

Component commissioning records in accordance with IEC62446;

Certificates of compliance for all electrical buildings;

IEC certificates of compliance for electrical components;

Geological survey;

Hydrological survey;

Topographical survey;

Chemical soil analysis; and

Training programme.

Appendices

<Below Appendices may form part of the Contract.>

Employer Provided Documentation List

Planning Documentation

Site layout;

Site location plan;

Decision notice;

Surveys requested by the Local Planning Authority (LPA) is applicable:

Construction Management Plan;

Noise Assessment;

Hydrology and Drainage assessment;

Construction Traffic Management Plan (CTMP); and

Landscape Ecological Management Plan (LEMP), etc.

Proof of discharge of pre-commencement conditions.

Land Lease documentation

Land lease/Option for Lease agreement; and

Site plan.

Grid Connection Documentation

Grid Connection Application;

Grid Connection Offer; and

Grid Connection Agreement.

Surveys

Ground Investigation Survey;

Topographical Survey; and

Utilities Survey.

RINA Tech UK Ltd. Queensberry House 106 Queens Roads Brighton, BN1 3XF, UK +44 (0)1273 819 429 rina.org.