| PV Technology Employer's Requirements - Solar PV |  |
| --- | --- |
| Draft |  |
| Triple Power Generation Limited |  |
| December 2025 | P0049208 – rev00 |

Issue and Revision Record Rev; Date; Originator; Checker; Approver; Narrative. 00; 12/12/2025; FG011, MRA06; AA021; FD020; Draft for Client’s input..

Disclaimer

This document has been prepared for the titled project or named part thereof and should not be relied upon or used for any other project without an independent check being carried out as to its suitability and prior written authority of RINA being obtained. RINA accepts no responsibility or liability for the consequence of this document being used for a purpose other than those for which it was commissioned. Any person using or relying on the document for such other purpose will by such use or reliance be taken to confirm his agreement to indemnify RINA for all loss or damage resulting therefrom. RINA accepts no responsibility or liability for this document to any party other than the person by whom it was commissioned.

As provided for in RINA’s proposal, to the extent that this report is based on information supplied by other parties, RINA accepts no liability for any loss or damage suffered by the client, whether contractual or tortious, stemming from any conclusions based on data supplied by parties other than RINA and used by RINA in preparing this report.

Contents

1	Solar PV Specific Scope of Work	6

1.1	General Technical Requirements	6

1.1.1	Supporting Documentation	7

1.2	Civil Works	7

1.2.1	Foundations for PV Arrays	7

1.3	Guaranteed Performance Ratios	7

1.4	Employer Provided Equipment	7

1.5	System Requirements	8

1.5.1	Solar PV Modules	8

1.5.2	Inverters	10

1.5.3	Inverter Positioning	11

1.5.4	Fixed Mounting Structures	11

1.5.5	PV Combiner Box	12

1.6	System Design and Installation Standards	13

1.6.1	Expected Life Span	13

1.6.2	General	13

1.6.3	Electrical Compliance	13

1.6.4	PV Specific Standards	13

1.6.5	Inverter Standards	14

1.6.6	Earthing Standards	15

1.6.7	Fuses in PV String Cables / Main Cables (Overload / Reverse Current)	15

1.6.8	Power Ratio Configuration	15

1.6.9	Connected DC STC Power	15

1.6.10	Exceeding Maximum Input Currents	16

1.6.11	Exceeding Connected DC STC Power	16

1.6.12	String Configuration	16

1.6.13	Low Voltage Distribution Boards	16

1.6.14	AC Load Switch Separators	17

1.6.15	Casings / Housings / Boxes	17

1.6.16	Buried Cables	17

1.6.17	Cable Trays, Cable Ladders, Pipes, Ducts	18

1.6.18	Module Mounting System	18

1.6.19	Cable Dimensioning (LV, DC and AC)	19

1.6.20	Shading	19

1.6.21	Equipotential Bonding	19

1.7	Health, Safety & Environment (HSE)	20

1.7.1	Noise During Operational Phase	20

1.7.2	Restoration of Site	20

1.7.3	Minimising Carbon Footprint	20

1.7.4	Presence of Livestock	21

1.7.5	Minimising Nuisance During Execution	21

1.7.6	Unexploded Ordnance (UXO)	21

1.7.7	Presence of High Voltage Lines	21

1.7.8	Safe Access to Electrical Equipment	21

1.8	Structural Engineering	21

1.8.1	Push Pull Tests	21

1.8.2	Perfo Soil Corrosivity	21

1.8.3	(Other) Underground Infrastructure	22

1.8.4	Wind Loading (Edges)	22

1.9	Security	22

1.9.1	Anti-Theft System	22

1.9.2	Security Arrangements (Operational Phase)	22

1.9.3	Security Arrangements During Execution	22

1.10	Stray Currents and Mutual Influencing of other Installations / Structures	22

1.10.1	General Requirements	22

1.10.2	Railways (If Applicable)	23

1.10.3	Underground Pipes	23

1.11	Maintainability	23

1.11.1	Space for Maintenance and Access	23

1.11.2	Storage Facility for Spares	23

1.11.3	Route and Row Markers	23

1.11.4	Usability of Documentation	23

1.11.5	On Site Identification	24

1.11.6	Numbering PV Tables	24

1.11.7	Access for Groundskeeping	24

1.12	Dynamic Power Control (Curtailment) and Reactive Power	24

1.12.1	Dynamic Power Control	24

1.12.2	Reactive Power Control and Stability to the Network	25

1.13	Requirements for Project Execution	25

1.13.1	Compliance with Engineering	25

1.13.2	Compliance with HSE Requirements	25

1.13.3	Avoidance of Damage to Third Party / Employer Property	26

1.13.4	Module Handling	26

1.13.5	DC Connectors	26

1.13.6	In Line Connections	26

1.13.7	Cable Lugs	26

1.13.8	Cable Management	27

1.13.9	Warnings / Labels	27

1.14	Inspection and Testing of Major Components	29

1.14.1	Factory Inspection and Testing	29

1.14.2	Pre-Shipment Factory Testing and Inspection	30

1.14.3	Production Witnessing of PV Modules	30

1.14.4	PV Module Independent Laboratory Testing	31

1.14.5	Cold Commissioning	33

1.14.6	Hot Commissioning	34

1.15	Documentation	34

1.15.1	Documentation Standards	35

1.15.2	Documentation Contents	35

A.	Initial Performance Test	37

A.1.	Purpose	37

A.2.	Performance Ratio	37

A.3.	Guarantee Values	37

A.4.	Test Duration and Conditions	37

A.5.	Eligible Data Points	37

A.6.	Availability During the Initial Performance Test	38

A.7.	Calculation of PV Cell Temperature	38

A.8.	Requirements for Successful Completion of the Initial Performance Test	38

A.9.	Initial Performance Test Report	38

B.	Interim and Final Performance Tests	39

B.1.	Purpose	39

B.2.	Guarantee Values	39

B.3.	Test Duration and Conditions	39

B.4.	Eligible Data Points	39

B.5.	Availability Test	40

B.6.	Interim and Final Performance Test PR Calculation Methodology	40

B.7.	Requirements for Successful Completion of the Initial Performance Test	40

B.8.	Interim and Final Performance Test Reports	40

C.	Final Acceptance Tests	40

C.1.	Visual Inspection Tests	41

C.2.	Functional Inspection Tests	41

# Solar PV Specific Scope of Work

The following Employer's Requirements are incorporated into the EPC Contract applicable to the construction of the Albrighton solar park (Contract).

The site layout is provided in the Project SharePoint (Site Layout Plan).

These Employer’s Requirements (ERs), contained in Part 2 of Appendix 11 of the Contract, detail the specifics of the Engineering, Procurement and Construction (EPC) Contractor’s scope of Work in relation to the Project. These ERs must be read in conjunction with the Employer's Requirements document titled "Employer's Requirements – General - Solar PV" contained in Part x of Appendix x of the Contract which describe and make reference to the minimum technical requirements for the Plant, including compliance, scope, design and execution requirements (PV Technology General ERs) and with the Employer's Requirements document titled "ICP Employer's Requirements - Solar PV" contained in Part x of Appendix x of the Contract (ICP Technology Specific ERs).

This section details the specifics of the Engineering, Procurement and Construction (EPC) Contractor’s scope of Work in relation to the Project. The Contractor’s general scope of Work is detailed in the General ERs document ‘P0049208_RINA_General ERs_Rev00.doc’.

The Contractor shall provide a “turn-key” solar photovoltaic PV power plant, including related infrastructure, to export the generated power to the local electricity network up to the nominated Point of Connection. The Facility shall be constructed in compliance with the terms and obligations of the Contract and this ERs.

## General Technical Requirements

The general Facility equipment and technical characteristics are provided in Table 1. This table is provided for guidance only and alternate specifications may be proposed by the Contractor.

Table 1: Assumed General facility and equipment characteristics

| Characteristic | Value |
| --- | --- |
| DC Power (kWp) | 49.16MWp |
| AC Power (kVA) (40°C nominal operating temperature) | XXXXX |
| Max. Export Capacity | 40MW |
| No. of modules | 80001 |
| Module Type | JAM66D45-640/LB |
| Dimensions | 2382mm x 1134mm x 30mm |
| Substructure Type | Piled |
| Modules per String | Varies |
| Number of Strings | XXXXX |
| Tilt Angle | 15* |
| Shading Angle | XXXXX |
| Azimuth from South | XXXXX |
| Inverter Model | SG350HX-16 MPPT |
| Inverter Power, kVA (40°C nominal operating temperature) | XXXXX |
| No. of Inverters | 125 |
| Nominal operating temperature DC/AC ratio on STC | XXXXX |
| Nominal operating temperature DC/AC ratio at the PoC (with grid limitation) | XXXXX |

### Supporting Documentation

The Contractor shall maintain and comply with all documentation detailed in the following section.

## Civil Works

### Foundations for PV Arrays

The Contractor shall design the foundations according to the mounting structure manufacturer’s requirements.

The Contractor shall provide a detailed structural analysis demonstrating that the design conforms to the contractual requirements and shall clearly state in its report the load assumptions, design specifications and design life.

In designing the foundations, the Contractor shall take into account all loads from the upper structures. The foundations and sub-structures shall be able to transfer all actual load combinations, including horizontal and uplift forces, safely to the foundation system with an appropriate factor of safety. The Contractor shall state in its calculations the maximum permissible foundation movement that may be tolerated consistent with normal operation of the Facility.

## Guaranteed Performance Ratios

- The Plant Performance Guarantee (including Performance Ratio and/or Energy Yield, as applicable) shall be calculated in accordance with the methodology set out in the relevant Schedule to the EPC Contract.

## Employer Provided Equipment

This Section has been included to cover situations whereby the Employer wishes to procure equipment itself under separate contracts. Solar PV modules, inverters, MVS units and SCADA will be Free Issued to the Contractor by the Employer.

Table 2 includes a list of equipment, which will be Free-Issued by the Employer and the location, and date at which Free-Issue will occur.

Table 2: List of Free-Issued equipment

| Contractor | Equipment | Delivery Point | Schedule |
| --- | --- | --- | --- |
| TBD at later stage | TBD at later stage | Address of delivery point | Schedule for delivery of equipment. If equipment is being delivered in multiple batches, delivery dates for each batch should be included here. It should be noted that failure to achieve these dates would allow the EPC Contractor to claim a Variation, so it may be worthwhile including some float between the date the equipment is meant to be delivered under the Framework, and the date included in this Table. |

## System Requirements

### Solar PV Modules

Modules will be supplied at a maximum DC voltage of 1500 V and will comply with following requirements:

The modules shall be of Tier 1 manufacturer and bankable;

The module shall have a positive initial power tolerance;

Crystalline silicon module efficiency shall be not less than 20% at STC and corresponding cell efficiency shall not be less than 22% at STC.  Module efficiency is defined as the ratio of the module output power to the intensity of incident solar radiation perpendicular to the surface of the Module including the frame;

Module efficiency at an irradiation of 200 W/m2 will be 96% or higher of the efficiency under STC;

Yearly degradation warranted shall not exceed 0.4%/yr;

LID shall not exceed 1.0%;

The connection box shall include at least 3 by-pass diodes to protect against partial shading and module overheating. Crystalline silicon modules must have flying leads fitted with at least IP67 rated pin type “Multi-Contact” (MC) connectors with copper conductors or equivalent with a clear indication of polarity for the connections. All connectors, including those at each end of the strings, will be of uniform type to prevent MC4 mismatch

Factory fitted module cables shall be long enough to allow the modules to be interconnected electrically in series to form strings;

The modules shall be capable of operating under extreme temperature (-40°C to +85°C) and humidity (5% to 95%) conditions and will be designed to ensure the highest possible reliability in operation and to ensure minimum and efficient required maintenance over the lifetime of the system. modules shall operate at the Site Conditions;

Each Module shall permanently display a technical characteristics nameplate carrying the following information as a minimum:

Name of manufacturer (or monogram or symbol);

Type or model number;

Serial number, barcodes to be placed on front and back;

Polarity of terminals or leads (colour coding is permissible);

Max system voltage;

Safety class;

Application class;

For class A modules the safety class II symbol;

Date and place of manufacture on label or traceable from serial number; and

The percentage power loss as a function of temperature (maximum power temperature coefficient) shall not exceed 0.45% per °C away from STC.

Flash test will be provided at 25°C for a minimum of four different levels of irradiance between 200 W/m2 and 1000 W/m2. The modules quality gain should be same or above the name plate capacity of the PV modules;

The solar cells within the modules shall be protected from mechanical stress and moisture via encapsulation in a plastic material of high clarity that is sufficiently flexible to allow contractions and expansions;

The Module must be certified for resistance to a suction pressure of 2400 Pa (Wind speed XX km/h with safety factor 3) and an increased distributed mechanical load of 5400 Pa on the front glass surface (wind, snow and ice);

The PV laminate (glass / encapsulant + solar cells / rear side) may be surrounded with a metal frame made of stainless steel or aluminium alloy; and

To avoid galvanic corrosion due to electrolytic action between different materials, any contact between different metals in the Module frame, if applicable, must be fully electrically isolated. The modules should be IEC 61701 salt a mist test complaint.

The modules shall come with a minimum product warranty of 25-years, and a minimum performance warranty of 25-years, but preferably 30-years.

The factory-leaving acceptance criteria of the module manufacturer shall be provided to the Employer for approval prior to any modules being dispatched from the factory. The site rejection criteria for modules delivered to Site shall be equivalent to the factory-leaving acceptance criteria. Specifically, modules containing dendritic micro-cracks shall be regarded as defective.

Modules must be handled carefully during the transportation and construction activities to avoid unnecessary additional micro-crack damage to the modules. Additionally, a module handling plan, covering all aspects of packing, transportation, reception on site, storage and installation is to be provided by the Contractor prior to shipping

Modules must be installed in accordance with the module installation manuals.

The Contractor shall provide evidence that the module manufacturer has measured flash test IMP currents of each Module and shipped modules with similar flash test results in batches such that modules with similar flash test IMP currents are connected in strings on site.

Modules’ Defects

Should any module display signs of any of the following issues, the module will be deemed to be defective:

Major cracks;

Discolouration of cells;

Water ingress;

Cell micro-cracks/snail trails – as per factory acceptance tests and as a maximum 6 cells per 72-cell module or if dendritic or if the crack electrically isolates 5% of one cell;

EVA or backsheet delamination;

Backsheet punctures/rips;

Metal corrosion or cracking/ broken interconnects;

PID;

Glass breakage;

Hot spots;

Junction box failure including adhesion/sealant failure;

Frame sealant gaps;

Cell mismatch causing the operation of the bypass diodes or affecting the output characteristic of the module (as evidenced in a stepped or otherwise affected I-V curve etc.); and

Bypass diode defects and/or failure.

The list presented above is not exhaustive.

### Inverters

The inverters may be either central or string and shall be rated to maximum DC input voltage of 1500V. The final choice of use of string or central inverter, and of DC voltage level, will be subject to Employer approval. Inverters will meet the following minimum requirements:

The inverter should be of Tier 1 manufacturer and bankable;

The inverter should be compliant to the local Grid Code and approved vendors;

String inverters shall be at least IP66 rated and shall be capable of being mounted such that they are installed under the Module arrays or specially constructed shades to prevent exposure from precipitation, ice melt and prevent exposure to direct sunlight;

Central inverters shall be installed in pre-fabricated lockable substations or in an outdoor installation. Electronics shall be protected with weather-proof material to at least IP66 protection degree and protected against corrosion and any other natural elements.

The inverters shall have proven track records in terms of performance, operation, and obtaining long term debt (international project finance), and the OEM shall have a proven track record for after sales support in the UK covering remote technical support and on-site technical support (if central inverters are used) and fulfilment of warranty claims;

The inverters provided shall have euro efficiency ≥98.80% and peak efficiency ≥99.00%;

The inverters provided shall have high reliability (expected availability ≥99%);

The inverters shall be capable of operating with Third Party monitoring systems. The inverters shall be capable of operating with Third Party monitoring systems; it is recommended to include additional specifications such as remote viewing of fault codes, remote restart capabilities, and for string inverters, specifying remote RISO testing and/or remote IV curve tracing capabilities;

The inverters shall be able to accept remote signals for the power quality regulation of such as active / reactive power and power factor;

The inverters shall be able to operate in a power factor range from 0.8 leading to 0.8 lagging and shall meet specific reactive power management requirements specified in the Connection Agreement;

Inverters will be designed to achieve Total Harmonic Distortion (THD) within limits specified in BS EN IEC 61000-3;

The inverters shall be equipped with;

DC fuses or circuit breakers;

Surge protection devices to protect inverters from AC and DC overvoltage. In general type II protection is sufficient. When connected with external lightning protection type I+II overvoltage protection is required in the AC installation and on the DC side of the inverters.;

An AC side automatic circuit breaker to protect and isolate the inverter;

Suitable ventilation; and

Integrated interface to allow for modifying operational parameters and displaying settings, main production variables, warnings, alarms, and faults.

Inverters shall be capable of operating in a temperature range of -25 C to +55 C and a relative humidity range of 5% to 95% and in the Site Conditions. This applies to individual inverters and assemblies with more than one inverter; and

Inverters should come with a minimum warranty of 10-years.

### Inverter Positioning

The placement of the inverters must meet the following requirements:

In accordance with the constraints and recommendations from the manufacturer as outlined in manuals or other documentation from manufacturer;

Inverter positioning should be easily accessible and should enable ease of operability and replacement;

If inverters are to be mounted on parts of an existing structure (walls, façades, …), a load bearing calculation according to the requirements of the Eurocodes must be carried out that demonstrates that the load bearing capacity of the structure is sufficient and the mounting method meets the requirements of the Eurocodes;

Sufficient space between the different inverters to ensure good ventilation, taking into account environmental conditions at the inverter location and the manufacturer specification;

Positioned to avoid direct sunlight;

Sheep grazing protection for sheep grazing areas;

When place indoors sufficient ventilation must be provided to ensure ambient temperature remains below 30°C;

Inverters must be easily and safely accessible for inspection, maintenance and replacement;

Risk of fire propagation must be minimised;

If the inverter is installed outside, the protection class must be at least IP65; and

Noise from inverters must be considered when determining inverter positions. Nuisance to neighbours, site users or other stakeholders must be avoided (see document ‘P0049208_RINA_General ERs_Rev00.doc’ specific section).

### Fixed Mounting Structures

The Contractor shall supply fixed tilt mounting structures oriented true South. The structures shall be made from aluminium, galvanised steel or Magnelis steel. Galvanisation coating thickness shall be suitable for the anticipated site-specific corrosion rates and designed to last at least 35 years. The mounting structures shall guarantee the prescribed tilt of the module plane and shall maintain this condition over the Facility’s design life (considering extreme and fatigue loadings).

The evaluation of the structural design of the mounting structures shall consider the selection of permanent loads, local area site wind conditions (XX km/h), seismic events, structural dimensioning and the control of the foundation, the sizing of members, the control of connections, and the effect of temperature changes and snow loads (if applicable for the location). The Contractor shall demonstrate that modules will remain attached to the structure under all environmental conditions reasonably expected at Site and that the maximum loading condition prescribed by the module manufacturer is not reached.

All connections including bolts, nuts, shall be of stainless steel or compliant with other industry standard practices appropriate for the application defined ensuring no corrosion risk. Fasteners that compromise the corrosion protection coating, such as self-tapping screws, shall not be used.

Pile saturation and pull-out tests (including but not limited to lateral, uplift and downward force) shall be completed in line with design requirements.

The module clamping system shall receive formal approval from the module manufacturer before commencing module installation. Sufficient space shall be left between module frames to allow for thermal expansion. Cable trays in mounting structure should have water drainage holes.

The fixed-mounting structures should come with a minimum product and corrosion warranty of 20 years.

### PV Combiner Box

If string combiner boxes (SCBs) are included:

Load switch separators must be installed to enable separation of the DC cables between SCB and inverter;

Positive and negative string leads must have fuses to prevent overload or damage from reverse current;

SCBs must be mounted so that all cable glands point downward at an angle of at least 15o from horizontal. Cables must point downward at the exit of the cable gland to avoid water ingress along the cables through the gland;

SCB design must be such that water accumulation on gaskets / access points is not possible in the intended orientation, to avoid water ingress in general and especially when opening access doors;

Condensation inside SCBs must be avoided by placing one way drain valves at the lowest point(s) of the SCB and vapor tight waterproof air vents at appropriate locations in the SCBs;

Note: SCBs must be of protection class II. This also implies that conducting parts (screws etc.) may not penetrate the housing;

SCBs will have the following characteristics:

Be CE certified;

UV resistant;

Be halogen free;

Feature protection isolation and be capable of fully isolating internal components;

Surge protection of at least Type 2 should be provided, including contact for operational detection;

Earthing touch protection;

Capable of operating in a temperature range of -25 °C to +55 °C and a relative humidity range of 5% to 95% and the Site Conditions;

Be capable of interfacing with a monitoring system based on an in/out DIN rail terminal block, using MODBUS RS485 protocol;

IP65 if installed outside;

CTs and PTs should be included for detecting string current and voltage;

CB temperature sensor; and

Protection to prevent direct contact with the busbar.

## System Design and Installation Standards

### Expected Life Span

The design of the installation should be based on a life expectancy of at least 40 years. Employer understands that inverters may have a shorter life expectancy;

All components must be new;

All components and assemblies must be suitable for the applicable climate class according to BS EN ISO 9223:2012, the minimum requirement is C3. Typically for locations less than 30 km from sea C4 is the minimum requirement. For locations within 1 km of the coastline C5 is required. In specific locations (e.g. industrial locations) C5 may also be required;

To prevent electrogalvanic corrosion direct or indirect electrically conducting contact between dissimilar metals must be avoided;

Components and assemblies must be able to withstand the expected environmental conditions (temperatures, UV radiation, …) during the design lifetime; and

Electro-galvanised material may not be used outside.

### General

NESC (ANSI C2), National Electrical Safety Code for Electric Supply Stations and Equipment;

BS EN 60950-1:2006+A1:2010, Information technology equipment- Safety –Part 1: General requirements;

BS 7671, Low-Voltage electrical installations (for topics not included in the National Electrical Standards and National Electrical Safety Code);

BS EN 62262:2002+A1:2021, Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts (IK Code);

BS EN 61936-1:2010+A1:2014, Power installations exceeding 1 kV AC;

BS EN 60529:1992+A2:2013, Degrees of protection provided by enclosures (IP Code);

BS EN IEC 60071-2:2018, Insulation co-ordination - ALL PARTS;

BS EN IEC 61850, Communication networks and systems for power utility automation –ALL PARTS; and

National Fire Prevention regulations.

### Electrical Compliance

Electrical compliance with BS 7671:2018 is a core requirement. This is applicable to all PV systems designed, built and implemented in the UK.

### PV Specific Standards

BS EN 60068-2-68:1996: Environmental testing — Part 2-68: Tests - Test L: Dust and sand;

BS EN IEC 60269-6:2011 + A1:2023, Low-voltage fuses – Part 6: Supplementary requirements for fuse-links for the protection of solar photovoltaic energy systems;

BS EN IEC 60721-2-4:2018 Classification of environmental conditions - Part 2-4: Environmental conditions appearing in nature - Solar radiation and temperature;

BS EN IEC 60891:2021: Procedure for temperature and irradiance corrections to measured I-V characteristics of crystalline silicon photovoltaic devices;

BS EN IEC 61215:2016, Terrestrial photovoltaic (PV) modules – Design qualification and type approval;

BS EN IEC 61345:1998, UV test for photovoltaic (PV) modules;

BS EN IEC 61701:2020, Salt Mist Corrosion Testing of Photovoltaic (PV) modules;

BS EN IEC 61724-1:2017, Photovoltaic System Performance Monitoring;

BS EN IEC 61730-1:2016, Photovoltaic (PV) module safety qualification - Part 1: Requirements for construction;

BS EN IEC 61730-2:2016, Photovoltaic (PV) module safety qualification - Part 2: Requirements for testing;

BS EN IEC 62093:2022, Balance-of-system components for photovoltaic systems - Design qualification natural environments;

BS EN 62446, Grid connected photovoltaic systems - Minimum requirements for system documentation, commissioning tests and inspection;

BS EN 62548, Photovoltaic (PV) arrays – Design requirements;

BS EN 62716, Ammonia Corrosion Testing;

BS EN 62738, Ground-mounted photovoltaic power plants - Design guidelines and recommendations;

BS EN 62759-1, Photovoltaic (PV) modules - Transportation testing - Part 1: Transportation and shipping of module package units;

BS EN 62790, Junction boxes for photovoltaic modules - Safety requirements and tests;

BS EN IEC TS 61836, Solar photovoltaic energy systems - Terms, definitions and symbols;

BS EN IEC TS 62804-1: Test methods for the detection of potential-induced degradation – Part 1: Crystalline Silicon;

BS EN IEC TS 63049, Terrestrial photovoltaic (PV) systems – Guidelines for effective quality assurance in PV systems installation, operation and maintenance;

BS EN 50380:2017, Marking and documentation requirements for Photovoltaic Modules;

BS EN 50521:2008, Connectors for photovoltaic systems – Safety requirements and tests;

BS EN IEC TS 62751, Photovoltaic (PV) arrays - Performance evaluation of partial shading;

BS EN IEC TS 62941, Photovoltaic (PV) systems - Requirements for testing procedures for the detection of infrequent defects;

BS EN IEC TS 62947, Terrestrial photovoltaic (PV) systems - Guidelines for the reduction of potential-induced degradation;

BS EN IEC TS 63035, Photovoltaic (PV) modules - Test methods for the detection of hot spots;

BS EN IEC TS 63043, Photovoltaic (PV) modules - Test methods for mechanical load resistance of framing system of photovoltaic modules; and

BS EN IEC TS 63105, Photovoltaic (PV) modules - Test methods for determining the resistance to circumferential mechanical forces of photovoltaic (PV) modules.

### Inverter Standards

BS EN IEC 62109-1: 2010 Safety of power converters for use in photovoltaic power systems – Part 1: General requirements;

BS EN IEC 62109-2: 2011 Safety of power converters used in photovoltaic power systems – Part 2: Particular requirements for inverters;

BS EN 50530: 2010 + A1: 2013 Overall efficiency of photovoltaic inverters;

BS EN IEC 62116: 2014 Grid-connected photovoltaic inverters – Test procedure for measures against islanding;

BS EN 61000-6-1: 2019 Requirements for electromagnetic compatibility;

BS EN 61000-6-2: 2019 Requirements for electromagnetic compatibility;

BS EN 61000-6-3: 2021 + A1: 2010 Requirements for electromagnetic compatibility;

BS EN 61000-6-4: 2019 + A1: 2010 Requirements for electromagnetic compatibility; and

BS EN 61000-3-11: 2019 Requirements for electromagnetic compatibility.

### Earthing Standards

IEEE Std. 80-2000, IEEE Guide for Safety in AC Substation Grounding;

IEEE 142-2007 IEEE Recommended Practice for Grounding of Industrial and Commercial Power System;

IEC 61936-1:2010+AMD1:2014, Power installations exceeding 1 kV a.c. – Part 1: Common rules;

IEC 60364-7-712, Solar photovoltaic (PV) power supply systems;

IEC 60999 (all parts), Connecting devices. Electrical copper conductors. Safety requirements for screw-type and screwless-type clamping units;

IEC 60071-1:2006, Insulation co-ordination - Part 1: Definitions, principles and rules;

IEC 60664-1:2007, Insulation coordination for equipment within low-voltage systems - Part 1: Principles, requirements and tests;

IEC 61557-8: 2014, Electrical safety in low voltage distribution systems up to 1000 V a.c. and 1500 V d.c. - Equipment for testing, measuring or monitoring of protective measures - Part 8: Insulation monitoring devices for IT systems; and

IEEE 81-2012- IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potential of a Grounding System.

### Fuses in PV String Cables / Main Cables (Overload / Reverse Current)

Fuses in PV string or PV array cables must be of type PV and suitable for the maximum current that can occur, calculated according to BS EN 60269-2:2013;

If the reverse current in parallel strings can be higher than the reverse current capacity of the modules, reverse current overload protection according to the requirements of BS EN 60269 must be in place (generally this is the case for 3 or more parallel strings. If 4 strings are switched parallel protection is always required);

If protection is provided by fuses both plus and minus string leads must both be fused. Every string in a parallel configuration must be fused;

All fuses in a parallel configuration must be of the same current rating and type; and

Use of diodes as overload / reverse current protection is not allowed.

### Power Ratio Configuration

The ratio between the maximum DC power of the inverter and the rated capacity of the combined panels must conform to the specification of the components, to be demonstrated by means of configuration calculations made in the latest version of the inverter supplier’s software developed for this purpose.

### Connected DC STC Power

The connected power (per input and per inverter) must be within the range specified by the manufacturer. Values outside the specified range require a waiver from manufacturer.

### Exceeding Maximum Input Currents

If the maximum input currents of the (individual inputs of the) inverter are exceeded, this must be taken into account in the yield calculations, and there must be a waiver from the manufacturer of the inverters stating that the configuration does not affect warranty or lifetime of the inverter.

Generally, an exceedance of specified current for Imp is acceptable, an exceedance of specified maximum current for Isc is not. A waiver must be obtained from manufacturer for any deviation, be it Isc, Imp or both.

### Exceeding Connected DC STC Power

If the maximum input DC STC power of the (individual inputs of the) inverter are exceeded, this must be taken into account in the yield calculations, and there must be a waiver from the manufacturer of the inverters stating that the configuration does not affect warranty or lifetime of the inverter.

### String Configuration

The string configuration must comply with the connection requirements of the inverter. Furthermore:

The open-circuit voltage in the longest string must be lower than the maximum input voltage of the inverter at the lowest expected cell temperature for the location (generally −10°C, lower temperatures may apply for specific locations); and

The maximum power voltage in the shortest and in the longest string must be within the maximum power voltage range of the inverter at NOCT (typically 55°C).

### Low Voltage Distribution Boards

The Low Voltage (LV) distribution boards, enclosures and all components used in the LV distribution boards must be suitable for continuous load at the total nominal power of the connected PV inverters under the expected worst case operational conditions. This can be demonstrated with heat load tests or calculations according to BS EN IEC 61439-1 10.10 (calculation according to IEC 60890);

The rating of the fuse holders must always be at least one step in current higher than the fuse that is to be installed. i.e. if a 160A fuse is used the fuse holder must be rated for at least 200 A. Higher over dimensioning of fuses and fuse holders may be required in specific circumstances, for example in cases of high heat load on the switch board / high expected ambient temperatures;

Continuous load on components may not exceed 80% of their nominal rating taking into account derating effects caused by heat loads from adjacent components. Exceptions to this rule can be made based on written statements from component manufacturers and / or verifications according to the first point of this clause;

Fuse holders must be suitable for use as load breakers, as demonstrated by their product specification;

It must be possible to lock fuse holders with external locks to implement a lock out tag out (LOTO) policy;

Cabinets for distribution boards that are placed outside must have at least protection class IP65;

Distribution board cabinets placed outside must be designed with an overhanging top to ensure there is no water accumulation between the access door and the cabinet body;

AC distribution boards must be mounted vertically;

Condensation inside distribution board cabinets must be avoided. Appropriate measures are Heating with thermostat, vapour proof and water tight one-way valves, drain valves; and

Fuse holders and/or load switch separators must be marked with a unique identifying number / code that is identical to the number / code on the inverter to which they are connected.

### AC Load Switch Separators

On the AC side, load switch separators must be installed, if these are not part of the inverter, they may be part of the low voltage switchboards if:

The fuse holders or automatic load breakers are suitable for use as load switch separators (this must be explicitly stated in the manufacturer product specification); and the devices used are suitable for following a lock out tag out (LOTO) protocol as required in BS EN IEC 60898, BS EN IEC 60715 and BS EN IEC 60947;

The time needed to walk from low voltage switchboard to inverter position is less than 5 minutes; and

There is no specific project requirement for load switch separators in the immediate vicinity of the inverters.

### Casings / Housings / Boxes

All casings must be suitable for the environment in which they are to be placed:

Casings must be mounted so that all cable glands point downward at an angle of minimally 15o. Cables must point downward at the exit of the cable gland to avoid water ingress along the cables through the gland;

Casing design must be such that water accumulation on gaskets / access points is not possible in the intended orientation, to avoid water ingress in general and especially when opening access doors;

Condensation inside Casings must be avoided by placing one way drain valves at the lowest point(s) of the casing and vapor tight waterproof air vents at appropriate locations in the casing;

Casings must be able to withstand the expected environmental conditions (temperatures, UV radiation, …) during the design lifetime;

Casings that are placed outside must have at least ingress protection class IP66; and

String wiring shall enter combiner boxes through conduit, cord grips, or other approved method that will properly seal the penetration and uphold the weatherproof rating of the combiner box.

### Buried Cables

In both Direct Buried or Ducted cables, a minimum of 100mm of sand all around the cable/duct is required for protection. A sand soil thermal resistivity ≤1.2Km/W must be used, and the ground conditions must be accounted for in the electrical calculations

Cables that are to be placed in soil must be suitable for direct burial, as demonstrated by their specification;

Mechanical protection must be provided either by using cables with a metal earth shield or by mounting cables in suitable conduits / ducts with sufficient impact resistance. Alternatively, protection may be provided by placing sufficiently wide plates or bands that provide impact resistance above the cables. This alternative may only be used after explicit approval by Employer;

Where cables are run within ducts or conduit, the mechanical protection must be appropriately sized to ensure thermal capacities are respected and to reduce resistive losses from the cables. The cables shall be protected from metal edges and openings. Underground cables must be protected from damage by termites, rats, mice, rabbits and other animals;

Bending radii of the cables should not exceed the minimum recommended by the manufacturer;

Cables must be buried at sufficient depth (generally 450 mm as best practice but some locations allow for 600 mm) to avoid damage;

Buried cables need to be ducted and should have a layer of tiles, boards or coloured plastic tape placed approximately 150 mm above them;

Buried cables from different parts of the installation (String Cables, DC string, DC Array, LV AC, HV AC, data) must be buried separately, each at their own specific depth;

Crossings of buried cables must be kept to a minimum;

Positions of buried cables must be clearly marked on drawings and traceable in the finished installation;

Cables are preferably buried in positions that remain accessible after completion of the installation; and

Consideration must be given to the use and future development of the area in which the cables are buried, examples are locations with traffic from heavy vehicles, locations where trees may grow, or buildings are planned.

### Cable Trays, Cable Ladders, Pipes, Ducts

Where the words ‘cable trays’ are used these must be read to include cable trays, ducts, cable ladders, pipes and any other tubular cable management solution;

Where cables cannot be mounted to module frames or mounting structure cable trays must be used to support and mount cables;

Mixing of cables that function at different voltage levels and/or have different functions is not allowed; DC cables, AC cables LV, AC cables HV and data cables must be in separate cable trays or, as minimum be separated by dividers in the cable trays;

Filling of cable trays may not exceed 70% by volume;

Filling of ducts may not exceed one third of its total volume;

Cables shall be fixed in the cable trays in such a way that damage caused by mechanical stress (caused by moving cables or the weight of the cables themselves) is avoided. Fixation method shall allow for (differential) thermal expansion and shrinking of cables and / or cable trays;

The cable trays must be positioned so that they do not contact the ground surface and must be supported sufficiently to prevent deflection;

Cut, sawn or ground ends of cable trays to be treated in such a way that they are protected against corrosion to the same level as the original part; and

All exposed cables should be UV resistant and outdoor rated.

### Module Mounting System

The module mounting system must allow for mounting the modules with full compliance to the requirements for mounting specified by the PV module manufacturer. Specifically clamping positions and clamp lengths must meet the requirements for the PV module and the pressure exerted on the module frames by the clamps must be below the maximum pressure specified by the PV module manufacturer;

For mounting frameless PV modules, the specific requirements specified by the PV module manufacturer must be followed with regards to choice of mounting system, clamp positions and clamp specifications. Explicit approval from the PV module manufacturer for the project engineering is required;

Where a reliable equipotential bonding of the module frames is not achieved by the connection to the mounting system additional measures must be taken to ensure reliable equipotential bonding of the module frames; and

The fixation method shall permit thermal expansion without transmitting excessive loads to the Panels.

### Cable Dimensioning (LV, DC and AC)

Cable current carrying capacity and cable losses must be calculated taking into account the cable type, chosen installation method and reduction factors for bundles and conductor dimensions as described in BS IEC 60287-1;

In addition to the requirements of above standards with regards to selection and dimensioning the following applies for maximal cable losses (voltage drop) in cables;

DC cables losses calculated at I = Imp,stc and conductor temperature of 75 oC must be less than 2% for central inverters and less than 1% for string inverters;

DC cable losses are calculated between last module connection and inverter input;

AC cable losses calculated at the rated current of the inverter and the maximum allowed conductor temperature for the selected cable must be less than 1.50%;

AC cable losses are calculated between inverter output and the point where gross production is measured;

The sum of cables losses AC+DC calculated with the methodology described above must be less than 2.00%; and

In specific cases (large installations with unfavourable form factors) higher cable losses may be allowed. This is subject to explicit written approval by the Employer.

In any case, cables to be designed for a minimum current of an over percentage 125% of maximum current of PV generator; and

For Bifacial modules, the 20.00% bifacial factor should be considered for sizing.

### Shading

Shading by external objects or parts of the PV installation must always be minimised regardless of the possible use of optimisers. When considering shading by plants / trees / shrubs their growth during the design lifetime must be taken into account.

### Equipotential Bonding

General

The load-bearing structure of the PV system must be equipotential bonded, metal cable ducts and PV modules with frame must also be bonded. This equalisation system must be connected to the Main Earthing Busbar (MEB) of the installation. The minimum conductor diameter for equalisation is 6 mm2 (if tinned copper is used). Equipotential bonding conductors shall be aluminium or tinned copper, bare copper will corrode and is not allowed. The main purpose of this bonding is to ensure the isolation resistance measurement and ground leakage function of the inverter can function properly. It also helps to avoid issues from electro-magnetic interference (EMI) If lightning protection is present refer to ‘External lightning protection’ below.

External Lightning Protection

If an external lightning protection system (LPS) is present on the building and the minimum separation distance cannot be observed, the frames and other conductive parts of this system must be connected to this in accordance with BS EN 62305.

Cable Trays / Cable Ladders / Cable Ducts

Cable trays or other components used for cable management must be equipotential bonded, or where applicable earthed. They may not be used as earthing / equipotential conductor.

## Health, Safety & Environment (HSE)

### Noise During Operational Phase

Although the installations are generally constructed in a rural environment and will generally be far from areas where people gather for longer periods, the risk of noise disturbance must be taken into consideration. In general, this only has implications for inverter selection and placement.

Inverter type should be selected for minimal noise production; and

Inverters should be placed far from residential areas other areas where noise disturbance could be an issue. This also includes recreation areas, foot paths etc.

### Restoration of Site

Use of the area as a solar PV site is foreseen to be temporary. After 40 years it is expected that the solar PV installation will be removed from the site. The site must then be restored to its original condition. Component selection and engineering must take this into consideration. This includes but is not limited to:

Materials must be selected that will not leach substances into the soil or leave residual material (flake, become brittle, …);

Using concrete blocks / pillars as anchoring of mounting structure is to be avoided. If the nature of the location (soil) makes using concrete anchoring unavoidable this is to be done only after explicit written consent from Employer and in such a way that concrete anchoring can be completely removed and easily separated from metal elements of mounting systems to enable separate disposal / recycling;

Foundations of transformer stations, other support constructions are to be constructed in such a way that they can be removed completely without leaving any residual material;

Access roads must be constructed in such a way that they can be removed completely without leaving any residual material;

Underground cables and cable protection must be constructed and placed to allow complete removal; and

Fencing and CCTV posts should adhere to the same principles, being designed and installed to enable their complete removal without leaving any residual material, ensuring a comprehensive approach to site restoration.

### Minimising Carbon Footprint

Concrete is a material with a very high carbon footprint and use of concrete for anchoring of the mounting structure should be avoided. If the nature of the location (soil) makes using concrete anchoring unavoidable this is to be done only after explicit written consent from Employer.

### Presence of Livestock

If grazing by sheep is planned on the location, or other animals are planned to be kept, the installation must follow the recommendation of the Guide BRE (2014) Biodiversity Guidance for Solar Developments from the BRE National Solar Centre.

### Minimising Nuisance During Execution

Access and egress from the build site and unloading activities must be carried out in a safe manner and must be organised to minimise obstruction of public roads and any pollution (mud) on public roads must be removed immediately during the construction phase.

### Unexploded Ordnance (UXO)

A study must be done to ascertain the likelihood of unexploded conventional explosives on site. Generally, this is done in the permitting phase. Municipalities have risk studies / maps that indicate areas that have a higher likelihood of finding UXO. If such a study shows there may be UXO on site, additional on-site research must be done to ensure there are no UXO or, if any are found, a pyrotechnic clearance shall be performed in accordance with the Guidance for unexploded ordnance in infrastructure activities (PI2016/01) by the British Defence Infrastructure Organisation (DIO) before any works begin.

### Presence of High Voltage Lines

The requirements defined by the work code (Electricity at Work Regulations Regulation 14) for working near High Voltage Lines are applicable if any work is to be done within the obstructed strip.

### Safe Access to Electrical Equipment

All electrical equipment must be safely accessible for inspection and maintenance, for ground mounted installations this also implies that the areas near this equipment may not become waterlogged, and measures must be taken to keep these areas reasonably dry.

## Structural Engineering

### Push Pull Tests

To assess load bearing capacity / pull out resistance and resistance to lateral movement of the soil push pull tests must be carried out on a representative sample of locations of the site. These tests must preferably be carried out with the piles that are foreseen for the PV installation and demonstrate that the design meets the requirements under the British Standards.

### Perfo Soil Corrosivity

When selecting protection measures / materials for piles and other underground components the soil corrosivity (acidity / salt levels) must be considered to ensure minimum required design lifetime is maintained.

### (Other) Underground Infrastructure

The presence of underground infrastructure (cables, pipes) must be investigated in a ground survey. This is done as part of the permitting process, and the results must be incorporated into the design of the PV site. Underground infrastructure in or near the site may necessitate additional measures with regards to stay currents / mutual influencing.

### Wind Loading (Edges)

The module tables on the outer edges of the PV field(s) are exposed to higher forces from wind loading. This must be taken into account in the design of the installation. Possible measures for PV module tables at the edges of the PV fields are:

Additional cross bracing of module tables for increased stiffness of tables;

Additional piles for better anchoring of tables; and

Additional module clamps on outer PV modules (lower edge / top edge / corners). This is especially important to prevent excessive module flexing that could cause micro cracks and increased module efficiency degradation.

## Security

### Anti-Theft System

A provision has to be made to ensure that any panels that can be easily accessed cannot be removed with normal tools. The contractor is free to offer an appropriate solution, final choice is subject to Employer approval.

### Security Arrangements (Operational Phase)

The site must be enclosed by a fence of at a minimum 2 meters high and with lockable gates suitable for access by heavy equipment (subject to the requirements of the construction permit). A continuous CCTV coverage of the entire perimeter fence and key internal areas using cameras with automatic motion detection and remote alarm to a permanently manned emergency response centre must be implemented. Additional requirements for insurance may apply and final choice is subject to Employer approval. Locks must, as a minimum, comply with security class RC3 according to BS EN 12209. Security class RC4 is advised for locks that are accessible to the public.

### Security Arrangements During Execution

Access to the building site, staging areas and storage areas must be restricted by suitable fences of at least 2 meters high. A CCTV system with automatic motion detection and remote alarm to a permanently manned emergency response centre must monitor access points and other critical areas such as storage areas. The solution shall be confirmed suitable by insurers.

Supply and installation of a site security system consisting of:

A remotely monitored CCTV system shall be provided for the surveillance of the perimeter fence and gates. Fixed position dual thermal and optical cameras built into one housing that are to be fitted to hot dipped galvanised bolt down foldable columns with predrilled holes for the mounting of the cameras and Power supplies. The columns will elevate at 3 metres, subject to planning conditions above ground level, positioned ideally 1 metre in from the perimeter fence. The cameras and poles will be installed in a clockwise rotation with each camera providing protection to the next camera in line with a maximum distance of 65 metres between columns. The camera systems shall be digital based systems which shall be user configurable, scalable, utilize digital storage devices and be connected to the monitoring facilities via a local area network. This system will also include an onsite audio challenge facility.

The Contractor shall be responsible for the design and positioning of CCTV cameras at strategic locations, mounted on buildings or using masts as required in the planning conditions, to achieve the full coverage of the perimeter fence and gates. Where the conditions do not state these requirements, the Contractor shall design the system considering long-range fixed position infrared cameras fitted to poles which will elevate at 3 metres above ground level and positioned 1 metre in from the perimeter fence. Each pole will be fitted with a camera providing adequate coverage with a tilt down function to alleviate any need for working at height to carry out any maintenance tasks. So that each camera provides protection to the next camera in line with a maximum distance of 65 metres between columns, depending on topography. The use of concrete shall be minimised for the installation of posts, ducts or draw pit cable boxes.

The overall design of the CCTV system shall be such that images of the subject of interest are captured, displayed and stored with sufficient resolution to enable a positive identification at any position within the area of coverage. The CCTV images displayed on the monitors shall be of adequate clarity to provide clear and unambiguous identification of persons or motor vehicles. Solid state CCTV cameras utilizing charge coupled devices (CCD) capable of providing high-definition colour video images shall be provided. Cameras installed in areas which are likely to be subject to changing light levels shall have lenses equipped with auto iris control facilities.

Infra-red lighting shall be provided for cameras where the level of illumination during the hours of darkness is insufficient to give a clear image. The beam width of the lighting shall be matched to the focal length and coverage of the camera. Infra-red lighting shall be switched automatically by photocells during the hours of darkness.

A digital storage system shall be provided capable of storing the CCTV images in time lapse or in real time modes as required. The images shall normally be stored in time lapse mode. The storage system shall have facilities to superimpose camera number and date/time data on the images.

The cameras shall be networked together using a dedicated local area network with sufficient segments to optimise the cabling requirements without compromising the system performance and throughput. The network cabling shall be tamper-proof.

Remote monitoring provisions in accordance with the latest General Data Protection Regulation (GDPR).

Should a security breach arise such that the CCTV becomes operational, the UPS should be capable of running for at least 6 hours.

CCTV cameras shall be located at all access points to provide clear identification of people and motor vehicles. The access control system is to include the provision of an audio challenge facility and can provide key holder response.

Keypads will be fitted to gated access points agreed with the Client.

## Stray Currents and Mutual Influencing of other Installations / Structures

### General Requirements

Corrosion from stray currents or touch currents on pipelines must be avoided. Where interaction is possible due to the presence of pipelines and or underground HV cables:

Identification, measurement and mitigation must be carried out according to BS 7671; and

Additional devices for monitoring of residual current may be required.

### Railways (If Applicable)

If parts of the site are near railways or cables will cross railways, technical advice can be provided by the Asset Protection and Optimisation teams (ASPRO) of the National Rail network.

### Underground Pipes

In order to make sure no third-party damage is caused to buried pipelines, the Contractor is advised to adhere to the ‘Requirements for the Siting and Installation of Solar Photovoltaic (PV) Installations in the Vicinity of Buried Pipelines’, defined by the UK Onshore Pipeline Operators’ Association (UKOPA).

## Maintainability

### Space for Maintenance and Access

The installation must be designed in such a way that there is sufficient space to carry out maintenance works on all parts of the installation and the supporting structures;

Especially for those components where regular access is required such as inverters, string combiner boxes and switchboards ease of access is key. These components should be accessible without the need for extra equipment or safety measures; and

The installation must be designed and implemented in such a way that access for maintenance and/or replacement of the site owner’s / tenant’s goods remains unhindered.

### Storage Facility for Spares

The storage facility for spares should ensure efficient and organized maintenance operations. It shall be equipped with clearly labelled sections for easy identification and retrieval of parts, minimizing downtime during repairs. The facility shall include an inventory management system to track stock levels and reorder parts as needed.

### Route and Row Markers

Route and row markers must be clearly visible to facilitate efficient maintenance, ensuring easy navigation and quick identification of sections within the site without obstructing access for routine inspections and repairs.

### Usability of Documentation

As built documentation should enable efficient identification and localisation of errors. This implies that:

There is a clear unambiguous connection between installation parts as identified in monitoring on drawings / diagrams in the as built documentation and in the real world;

String plans show correct localisation and identification of strings with the same coding as applied on the strings at the inverter input;

Documentation of monitoring should be clear, complete and accurate and include IP addresses of components / gsm numbers and protocol specifications; and

All documentation will be available in English, in their native format (e.g. .docx, .dwg) and PDF.

### On Site Identification

The relationship between items in monitoring, as-built documentation and the real situation in the installation must be clear and unambiguous. Where necessary, for example at beginnings and ends of strings Contractor should place string labels with string number and polarity.

### Numbering PV Tables

All PV table rows must be marked with a clearly visible table row number at both ends. The numbering must correspond to the numbering in the as built project engineering. Where table rows are intersected by maintenance roads or similar additional markings must be placed as appropriate.

### Access for Groundskeeping

The entire installation including cabling, inverters, string combiner boxes and other components must be designed and executed in such a way that mowing with manned machines is possible without risk of damage to any part of the installation.

## Dynamic Power Control (Curtailment) and Reactive Power

### Dynamic Power Control

There is a requirement for (remote) control of the output of the PV installation because of grid capacity limitations and/or energy market incentives. In that case a reliable dynamic power control system (DPCS) must be implemented. The DPCS must ensure that the current at the critical point in the installation (point with lowest current carrying capacity, either because of grid capacity restriction or component dimension) remains below the maximum allowed current.

This system must comply to the following requirements:

Reliable functioning: The DPCS must function reliably within the set parameters. If the DPCS loses functionality or communication to (parts of) the PV Site is lost, the inverters that are managed by the DPCS must automatically switch to a safe mode (reduced maximum power). Power reduction must be such that overload of cables or grid connection cannot occur;

Dedicated CTs PTs should be available at PoC for Plant power controller;

The fail-safe working of the system must be tested during testing period and logged in the test and commissioning document;

Set points and controls: Set points, control loops and other relevant parameters of the DPCS must be remotely adjustable. Accidental or unwanted change of the DPCS parameters must be impossible;

Currently allowed setpoint interface protocols: ModbusTCP and DNP3.0;

Traceability: The impact of down regulation on the performance of the PV installation must be traceable. To this end one or several inverters must operate independently of the DPCS to enable a comparison of performance with – and without control. The settings of the DPCS and the total combined power of the independently operating inverters must be such that overload of the (HV) cables, grid connection or other components cannot occur;

Monitoring: Activation times and set points of the DPCS must be communicated to the monitoring system to ensure performance of the PV installation can be monitored;

Requirements for Generators (RfG) compliance: The DPCS must be RfG compliant / May not adversely influence RfG compliance of the PV installation; and

The functionality of the DCPS and the Energy Management System must be fully integrated to ensure optimal energy flows and to ensure the combined systems (PV and EMS) do not cause overload of cables or grid connection.

### Reactive Power Control and Stability to the Network

Controlling Reactive Power

The system must comply with the voltage regulation mentioned in the Grid Code for installation with PV inverters and UPS batteries if any, including flicker and voltage unbalance assessments in accordance with ENA Engineering Recommendations P28 and P29, harmonic studies as per ENA Engineering Recommendation G5/5 and ENA Engineering Recommendation G99 power system studies. The voltage regulation must be performed by the inverters to reduce the limitation of active power due to this constraint.

The contractor must ensure that the reactive power control design does not affect the plant's nameplate capacity and that peak real power is maintained under standard conditions, in accordance with Grid Code limits.

Additional regulation is contained within the Grid Connection Agreement and should be adhered to.

Regulating the production of reactive power between PV inverters and UPS batteries if any, must be done by the DPCS.

Resistance to Pressure Trough and Decoupling Protection

Particular attention will be paid to the holding voltage dips of the complete system (PDL, transformers, inverters, SCADA, DPCS ...), as the technical standards in force. The decoupling protections will be tailored to the specific rules of the distribution network operator, territories and installed capacities. The installation as a whole must remain functional outside disconnection beaches and respect the rules and standards, as well as local technical specifications of the distribution network manager.

## Requirements for Project Execution

### Compliance with Engineering

Project execution must be in complete accordance with the approved engineering and the PV Technology General ERs document ‘P0049208_RINA_General ERs_Rev00.doc’.

### Compliance with HSE Requirements

All activities and work methods must be in full compliance to the HSE requirements for the project and the requirements in PV Technology General ERs document. Specifically:

Appropriate and functional PPE;

Safe working at heights;

Safe working in (on) electrical installation;

Ensuring safety of third parties; and

Keeping a tidy workplace.

Wheel Wash facility must be provided.

Roads kept clean throughout the construction Period

Refer the EP SHEQ Minimum Standards document.

### Avoidance of Damage to Third Party / Employer Property

Damage to the property of the owner or third parties must be avoided. This includes, but is not limited to:

Making detailed plans for storage of materials and transport of materials to and from the work place;

Placing protection on surfaces or other items that could be damaged during project execution; and

Ensuring sufficient free space for material handling.

### Module Handling

Module handling must be in full compliance with the manufacturer instructions and the handling requirements in PV Technology General ERs document.

### DC Connectors

Connectors must be of the same brand and type. Cross mating (mating of different brand/ type) of connectors is not allowed;

Gland nuts must be fastened to the required torque (manufacturer specification) and the gap between connector body and gland nut must be of uniform width (no cross threading / crooked mounting);

The first 20 mm cable at the connector gland must be straight and in line with the connector;

Connectors must be mounted / fixed to avoid excessive movement due to wind;

Connectors must be mounted / fixed in a position that minimises exposure to the elements; and

Where exposure to the elements is unavoidable connectors must be fixed in a horizontal position to avoid water accumulation on gaskets in gland nuts.

### In Line Connections

In line connections in cables are not allowed

### Cable Lugs

Cable lugs must be suitable for the conductor diameter used;

Cable lugs and pressing must be suitable for the conductor type (specifically (single); stranded-round and (single) stranded-sector may require different pressing / cable lugs);

Cable lugs must be suitable for the conductor material (Copper or Aluminium) and the bus bars (e.g. for Aluminium conductors bimetal lugs must be used);

If Aluminium conductors are used suitable contact lubricant must be applied on the conductor / in the lug insert;

Pressings of cable lugs must be according to the manufacturer specification for the combination of lug and conductor diameter (hexagonal / indent, size, width, number and position on lug);

Single and multi-stranded sector shaped conductors must be rounded with a suitable round press insert prior to insertion in the cable lug, for copper sector shaped multi stranded conductors generally sleeves must be used (see cable lug specification for details);

Pressings must remain visible for inspection. Use of heat shrink tubing on cable lugs is generally not recommended. If heat shrink tubing is used this must be transparent to allow visual inspection of the cable lug pressings; and

Cable insulation must end as close as possible to the bottom of the cable lug. Ideally no uninsulated conductor is visible at the point where the cable is inserted into the lug.

### Cable Management

Mechanical stress in cables must be avoided under all circumstances that occur during normal operation. This implies that:

At bends or changes in direction there must be sufficient slack in the cable(s) to ensure there is no mechanical tension or contact with sharp edges or points at the lowest temperature that will occur on the location;

The minimum bending radius of cables must be maintained under all circumstances. If the cable manufacturer does not specify a minimum bending radius, five times the outer diameter of the cable shall be used as minimum bending radius;

Cables shall be laid parallel wherever possible and cable crossings shall be kept to an absolute minimum;

Where cables cross sharp edges or points and sufficient distance between cable and sharp edge / point cannot be guaranteed suitable and durable edge protection must be placed;

DC cabling between / underneath modules must be attached to the modules or mounting system to avoid damage to cables or connectors (wind action, grinding on surfaces / edges); cabling in cable trays must be fastened at regular intervals appropriate to the flexibility of the cables. Maximum distance between fastening points is 3m;

The risk of induced voltages from (indirect) lightning strikes must be minimized by placing plus and minus DC leads as close to each other as possible (BS 7671:2018 and BS EN 62305); and

Special attention must be given to avoiding strain on input terminals of inverters, especially when the inverters are not vertical and/or Y connectors are used. Cables must be supported to ensure the weight of free hanging cables, Y connectors, fuses, or other components in line with – or attached to cables does not put a transversal force on the terminals. This means Y connectors and in line fuses in DC string cables must be supported in a cable tray or similar.

### Warnings / Labels

General

All labels and warnings must be in English.

All labels and warnings will be sufficiently durable and suitable for the conditions in which they are placed:

Remain clearly legible for the lifetime of the PV Site;

Remain attached for the lifetime of the PV Site; and

UV/weather resistant

See standard BS EN ISO 7010:2019 for all labels.

Grid Connection Point

At the grid connection point, electricity meters and switch boards to which inverters are connected the label below (or a similar label) must be placed. If connection point and/or switch board and/or electricity meters are at the same location one label at that location suffices.

DC Access Warning

Each access point to active parts on DC-side has to be marked with an indication: ‘PV installation -DC- Active parts can still carry voltage after switching off’.

Inverters

All inverters must have a warning sign indicating that they must be separated on both DC- and AC-side before maintenance activities.

Inverters must be marked with a unique identifying number / code.

String Combiner Boxes

All string combiner boxes must be marked with an indication: ‘PV installation -DC- Active parts can still carry voltage after switching off’.

String combiner boxes must be marked with a unique identifying number / code that has a one-to-one correspondence with the inverter numbering.

Coding of DC Cabling

All DC cabling must be coded logically in a uniform manner (inverter / string combiner box number, string number, polarity). Coding must be durable and is to be applied at the inverter connection point, string box connection point (if applicable) and at the connection points (plus and minus) of string cables to PV module cables.

Coding of Fuse Holders / Load Switch Separators for Inverters

Fuse holders and/or load switch separators must be marked with a unique identifying number / code. For fuse holders / load switch disconnectors of inverters the number / code must be identical to the number / code on the inverter to which they are connected.

Transformer Stations / Switch Boards

Appropriate warning signs as required (Typically ‘Danger High Voltage’) and / or the icon below must be mounted at access doors.

## Inspection and Testing of Major Components

The Contractor shall be responsible for conducting all tests in such a way as to protect the safety of all persons and the Works and in accordance with relevant Law. The Contractor shall provide an appropriate training for all personnel on the Site who will be involved in or witnessing any tests and shall ensure that such personnel comply with all applicable safety procedures at all times during performance of the Tests. The Contractor shall discontinue performance of any Tests in the event of any unsafe conditions.

The Contractor is responsible for all equipment, materials and labour required for testing. In the event of failed tests, the Contractor is responsible for rectification and re-testing until the test is passed. The Contractor shall provide all reports, calibration/test certificates and documentary evidence required by the Employer to verify all tests have been passed.

### Factory Inspection and Testing

Upon finalisation of preferred equipment suppliers, the Contractor shall advise the Employer as to the location of manufacture of each of the key equipment items including (modules, mounting structures, inverters, transformers, HV switchgear, prefabricated buildings and others as reasonably requested by the Employer).

The factory inspection aspect of the Inspection and Test Plan shall include as a minimum:

All tests required by relevant Standards;

Location of manufacture;

Scope of activities undertaken at the facility;

Review of production machines and key components ‘suppliers and certifications;

Materials/equipment supply contracts;

Technical review of materials/processes;

Review of certifications for bill of materials, and in particular, confirmation that they relate to the bill of materials to be used for the relevant production run;

Factory quality: including processes, certifications, quality control, levels of automation and staffing, health and safety records, ingoing and outgoing QA procedures and production tolerances.

Quality control criteria and processes, including track record of warranty claims;

QA statistics and recall volumes including reasons for recall (e.g. materials, manufacturing, design, shipping), including outcomes of recall process;

Factory inspection and acceptance testing of components to be shipped, included procedures for rejection of equipment if faults are identified;

Finished goods management including sorting and packaging procedures for the relevant Materials; and

Type test certificates for the combiner boxes, inverter stations and switchgear shall be provided to show compliance with the Relevant Standards.

### Pre-Shipment Factory Testing and Inspection

The Contractor shall undertake pre-shipment testing and inspection upon completion of manufacture and prior to shipping. The Contractor shall submit a FAT schedule to the Employer and confirm the actual date 2 weeks before the FAT happens, allowing the Employer or the Employer’s Representative to witness the FAT.

Factory Inspection Test (FAT) certificate completed during the manufacturing assembly and testing of inverter station equipment, power stations, solar PV modules, cables, switchgears, substation equipment, SCADA, protection panels, transformers, steel works and module structure shall be forwarded to the Employer for approval.

Pre-shipment acceptance criteria of the major equipment manufacturers shall be in the ITP.

As an example, the pre-shipment testing of modules shall incorporate the following tests, in accordance with IEC 61215, to be completed on a 100% sample:

Visual inspection;

Electroluminescence (EL) testing;

Maximum power determination or ‘flash’ testing; and

Insulation test.

The Contractor shall supply the Employer with Test Results for the above-mentioned tests that shall include flash tests results and electroluminescence images in electronic format for all modules.

Gel contents tests shall also be performed on a sample of Modules.

### Production Witnessing of PV Modules

The Employer shall have the right to inspect and witness production processes at all module factories. The Inspection and Test Plan (ITP) shall identify specific witness and hold points that the Employer should attend;

The Employer reserves the right to bring Third Parties during such inspections;

The sample size and Acceptance Quality Level (AQL) shall follow ISO2859. Lot size is [XX] MWp;

A critical defect is a defect that materially affects the performance of the PV module;

A major defect is one that affects the performance of the PV module; and

Minor defects do not affect long-term performance.

Table 3: Tests at PV module manufacturer’s factory

| Test name | Sample Size | AQL | Acceptance Criteria |
| --- | --- | --- | --- |
| Visual Inspection | General Inspection Level 2 | Critical defect: 0 Major defect: 1 Minor defect: 2.5 | To be provided by the Contractor for each type of defect. |
| Electroluminescence (EL) testing | General Inspection Level 2 | 0 | To be provided by the Contractor for each type of defect. |
| Electrical performance at STC (IV test) | General Inspection Level 2 | 0 | As per datasheet. |
| Power bifaciality coefficient | Special inspection Level 4 | 0 | As per datasheet/OEM documentation. |

### PV Module Independent Laboratory Testing

- If the Contractor is supplying modules, this section shall apply to its scope.

A quantity of Test Modules to be agreed, based on a sample sized in accordance with ISO 28590:2020, shall be subjected to Third Party testing;

The Test Modules shall be randomly selected from the production-line producing the modules for the Plant, and evenly spread across the production batches, such that at least every batch and every shipment is represented by the sample;

The Third Party testing shall be performed at an internationally accredited, temperature-controlled and calibrated laboratory (to be agreed with the Employer) specialising in the testing of modules; and

The modules shall be subjected to the non-destructive tests as provided for in IEC 61215 or IEC 61646 (as applicable), or as agreed between the Contractor and the Employer prior to testing. For the avoidance of doubt – the modules will be subjected to electroluminescence testing at 10% and 110% of the module forward-bias ISC with the resultant high-resolution images being part of the Test Data provided to the Employer. The tests shall include as minimum:

Table 4: Tests at independent laboratory

| Test name | Sample Size | AQL | Acceptance Criteria |
| --- | --- | --- | --- |
| Electroluminescence (EL) testing | General Inspection Level 2 | 0 | To be provided by the Contractor for each type of defect. |
| Electrical performance at STC (IV test) | General Inspection Level 2 | 0 | As per datasheet. |
| Power bifaciality coefficient | Special inspection Level 4 | 0 | As per datasheet/OEM documentation. |
| Resistance to PID | General Inspection Level 2 | 0 |  |

After testing, the Test Modules shall be shipped to site and incorporated into the Works at specific locations to be agreed explicitly with the Employer; and

All costs associated with testing shall be deemed to have been included in the Project Price.

Where a PV module does not pass the acceptance criteria for a test, this PV module shall be replaced by another PV module which passes the respective test. In case a Lot of PV modules is not accepted per the Acceptance Criteria the Contractor shall retest the lot using a sample size in line with their Quality Plan.

#### Visual Inspection

The purpose of this test is to detect visual defects in the front and rear surface of the modules.

The procedure shall involve inspection both sides of the module under an illumination of not less than 1000 lux for the following defects:

Cracked or damaged surfaces;

Potential damage or discoloration;

Bent or misaligned external surfaces;

Cracked or broken cells;

Snail trails;

Broken, faulty interconnections;

Cell touching one another or frame;

Failure of adhesive bonds;

Evidence of any molten or burned component;

Bubbles or delamination;

Exposed or short-circuited electrical parts; and

Damage to module sealing or frame.

#### Electroluminescence Test (EL Test)

All sampled modules will be subject to EL testing by an accredited and independent third party. The third party will evaluate images for cell damage and micro-cracks per industry accepted standards. The EL images shall be provided by the manufacturer for all modules sampled under visual inspection and reviewed by a third party.

#### Resistance To PID

The modules are to be tested in accordance with IEC 62804 standard at 85° Celsius, 85% humidity, 96-hour duration and voltage bias of 1500V. Control test measurements are to be conducted before and after PID tests such as Electroluminescence (EL) and Maximum Power Determination (Pmax) at STC (IEC61215: 2016). Pmax at STC to be equal to or below 5% loss of the rated nameplate power.

#### Bill of material verification

The EPC Contractor shall provide the independent third party and the Principal with the BOM and necessary information to verify the BOMs used are IEC61215 and IEC61730 certified and compliance to the agreed BOM.

Testing of the PV plant for commissioning will be according to the specific requirements of the contract and norms and standards defined in Section 12 of the General ERs.

### Cold Commissioning

The following tests and measurements shall be done and successfully passed by the Contractor prior to Cold Commissioning, as specified in the standard BS EN IEC 62446:2020.

Checking of the compliance of cross section of all cables with the technical specification;

Measurement of insulation resistance of AC cables between;

Main Low Voltage Switchboard and transformer ESS (if any);

Main Low Voltage Switchboard and inverter(s);

Transformer ESS and ESS inverter(s).

Measurement of insulation resistance of DC cables between PV modules and inverters;

Measurement of open circuit voltages and polarity check of all PV strings at string interconnection;

Measurement of ground resistance of all buildings and equipment (for inverters) and the mounting structure and modules’ frames;

Transformer commissioning tests (winding resistance, insulation resistance, dielectric strength measurements, etc.); and

Verification of the conformity of the point of connection security and connecting / disconnecting equipment in compliance with the network operator requirements in order to authorise the grid connection.

No-production Commissioning of the Power Plant

The following tests and measurements shall be done and successfully passed by the Contractor for No-production Commissioning validation.

Verification of the electrical supply of all auxiliary equipment, including (but non-exhaustive) inverters, PLCs, computers, SCADA, internal lighting of every room and spare sockets;

Verification of the functioning of all auxiliary systems, including (but non-exhaustive) ventilation and heating systems (HVAC) if any;

Verification of the communication of all connected equipment;

Verification of the distant network access with check of the switch to the security connection in case of failure of the primary connection;

Metering point and transformer conformity tests including (but non-exhaustive) its communication with SCADA and the sending of all required alarms, switchgear automatic and manual operation tests, UPS functioning and battery capacity check if any; and

Inverter commissioning and start-up check, in particular the parametrization in conformity with grid-code requirements and norms and references (among all G99).

SCADA Test

The general functioning of the SCADA will be tested and checked separately:

Connection to the SCADA; and

Verification of the good communication.

Visual Inspection

The Contractor shall perform a visual inspection of each PV module including rear surface, front surface, junction boxes, frames, cables and connectors. The following criteria shall determine a failure:

Cracked, bent or damaged external surfaces;

Broken or cracked cells;

Faulty interconnections;

Cells touching one another of the frame;

Failure of adhesive bonds;

Exposed live electrical parts, faulty termination; and

- Any other conditions which may affect performance as advised by the Original Equipment Manufacturer.

Any identified defects or rectification of a defect shall be recorded with the following information:

Position;

PV module serial number of defective module and replacement module;

Description of the defect/remediation observed;

Date of detection of the defect;

Photograph or hyperlink to photograph of the defect/remediation; and

Date of the remediation works/replacement.

### Hot Commissioning

During the Hot Commissioning of the Solar Plant, the following items shall be checked:

Inverters as per the commissioning procedure provided by the manufacturer and validated by the Employer;

Metering point conformity tests;

IV Curve test;

SCADA data acquisition and displays;

Drone thermography;

Verification of the functioning of all auxiliary systems during operation, including (but non-exhaustive) ventilation and heating systems;

The conformity of the weather station and all sensors (pyranometer, anemometer, temperature sensor) as well as module temperature sensors if any; and

Communication tests between the PV plant and the grid operator systems.

The list above is not exhaustive. The Contractor must carry out all tests necessary to ensure the total compliance of the plant with the requirements of the Employer, Grid Operator and the appropriate norms in force.

## Documentation

A master documentation list is to be provided by the Contractor for all the designs and documents they will be providing to the Client.

All documents are to be in English and be available in both native format (e.g. .dwg, .xlsx) and PDF.

### Documentation Standards

Basic documentation must as a minimum be in accordance with:

Table 5: Documentation standards

| Requirements | Standard |
| --- | --- |
| High Voltage Installation | BS EN IEC 61936-1:2021 |
| Switch Boards | BS EN IEC 61439-1:2021 section 6.2 |
| PV Installation | BS EN IEC 62446-1:2016 part 4 |

### Documentation Contents

Documentation will include at least:

Static strength calculation of the PV module mounting constructions (stability, wind load, and snow load);

Cable calculations;

Safety study with settings for the protection devices of the HV installation;

Annotated electrical drawings and specifications of switch boards (HV and LV);

Plan view and front view of switch boards / gear / transformer stations. Side views of equipment as needed;

Full specifications of transformer stations, HV switchgear, LV switchgear;

Electrical drawings for HV and LV installation (annotated SLD with cable dimensioning, protection devices and their setting, load breakers, … indicated);

Data sheets, manuals, and guarantee certificates for the inverters, transformers and switchgear;

Data sheets, manuals and guarantee certificates for the PV panels;

Waivers from manufacturers and notices of acceptance of deviations from Employer;

Single-line drawing of the DC installation showing at least the following;

String configuration (number of strings per inverter and string length);

Diameter and length of string cables;

Combiner boxes, fuses and overvoltage protections; and

Equipotential bonding;

Lay out of the installation showing the individual strings with string numbering, table numbering, positions of combiner boxes, inverters, transformers, … corresponding to the numbering in the single-line diagram so that the position of each string in the installation can be determined unequivocally;

Cabling plan in which the location and method of installation (cable ducts, channel, buried, etc.) of all cables is clearly marked;

Maintenance manual, with start-up and stopping and emergency procedures;

Error and fault message procedure;

Results of completion inspections, measurements and functional tests;

Test results all component tests (FAT, SAT);

Flash test data of all installed modules;

Itemised list of spares; and

Contracts, permits and engineering / civil / environmental or other studies for the project.

### Earthing

Earth ring main to be installed throughout the site.

Fencing CCTV and Gates to be earthed as required

All tables to be connected to the ring main earth cable

All tables to be ring main earth cable linked and labelled

All inverters and AC Isolators to be Earthed including AC LV Cables and linked back to the earth leg.

All transformers to be connected to the ring main earth cable.

CSS and DNO are to have earth matt installed and connected in accordance with the approved earthing design.

FOP test to be undertake and witnessed by the DNO

FOP test report to be submitted to the DNO for approval

Initial Performance Test

Purpose

The Contractor shall carry out the Performance Test for the Solar PV Plant. The test procedure, methodology, measurement parameters and acceptance criteria shall be as defined in the relevant Schedule of the EPC Contract.

Performance Ratio

The Performance Ratio (PR) is the measurement of quality of the design, components and installation of the system. It is defined as the ratio between the actual energy produced and the energy that could theoretically be produced before any system loss.

- The detailed methodology for calculating the Performance Ratio shall be defined in the relevant Schedule of the EPC Contract.

Guarantee Values

For a successful Initial Performance Test, the Performance Ratio calculated over the Initial Performance Test period (PRInitial) must meet or exceed the Guaranteed Performance Ratio.

The guaranteed value of the Performance Ratio shall be specified in the EPC Contract.
Compliance with the guaranteed value shall be verified through the Performance Test conducted in accordance with the procedures defined in the EPC Contract Schedule.

Failure to achieve the guaranteed Performance Ratio shall be subject to the remedies set out in the EPC Contract.

Test Duration and Conditions

The Performance Test shall be conducted following completion of commissioning and achievement of mechanical completion of the Solar PV Plant.

The test shall be carried out over a continuous test period, the duration of which shall be specified in the EPC Contract Schedule.

The Performance Test shall be conducted under stable operating conditions, with the Solar PV Plant operating normally and without curtailment, grid restrictions, or abnormal operating conditions, except where otherwise defined in the EPC Contract Schedule.

The Contractor shall ensure that all measurement equipment used for the Performance Test is properly calibrated and installed in accordance with applicable standards and good industry practice.

Eligible Data Points

Only data points that meet the validity criteria defined in the EPC Contract Schedule shall be considered eligible for the Performance Test evaluation.

Eligible data points shall generally include measurements recorded during periods when:

the Solar PV Plant is operating under normal operating conditions,

the irradiance and meteorological measurements are within the acceptable measurement range of the installed sensors,

all relevant monitoring systems and meters are functioning correctly and

no operational restrictions, abnormal events, or external curtailment affect plant performance.

Data points recorded during equipment failure, grid outages, curtailment, or abnormal plant operation shall be excluded from the test evaluation

.

Availability During the Initial Performance Test

During the Performance Test period, the Solar PV Plant shall maintain a minimum operational availability level, as defined in the EPC Contract.

Plant availability shall reflect the proportion of time during which the generating units and associated electrical systems are capable of operating and exporting power under available irradiance conditions.

Periods during which equipment is unavailable due to Contractor-related faults may be excluded from the test period or otherwise treated in accordance with the provisions of the EPC Contract.

Calculation of PV Cell Temperature

The PV cell temperature shall be calculated in accordance with criteria defined in the EPC Contract Schedule.

Requirements for Successful Completion of the Initial Performance Test

The Initial Performance Test will be considered as successfully completed if the conditions set out in the relevant Schedule of the EPC Contract are met.

Initial Performance Test Report

A test report shall be prepared and submitted to the Employer summarising the methodology, procedure, details and results of the test.

Processed data shall be prepared in an Excel spreadsheet with the following columns:

Date and time;

Global inclined irradiance measured for each GII pyranometer;

Global inclined irradiance calculated mean value;

Ambient temperature measured for each ambient temperature sensor;

Ambient temperature calculated mean value;

PV cell temperature calculated with the thermal model;

Measured energy production measured at the revenue energy meter (meter output);

Performance Ratio (calculated);

Each string combiner box power;

Total inverter power; and

AV (calculated).

Each day of the test will be represented with a summary of data over the course of the day. An additional summary will combine data over the whole Test Period. The spreadsheet will be readable by the Employer for the purposes of auditing.

Interim and Final Performance Tests

Purpose

The purpose of the Interim Performance Test and Final Performance Test is to quantify the performance of the PV plant relative to its Performance Guarantees over the first and second operating years, respectively.

Guarantee Values

The Guaranteed Performance Ratio for the Interim Performance Test and Final Performance Test (PRInterim and PRFinal) are provided in Section 1.3.

Test Duration and Conditions

The commencing and finalisation of the Interim Performance Test and Final Performance Test shall be agreed by the Parties to the test, in compliance with the Contract.

The duration of the Interim Performance Test shall be the 12-month period from the date of Completion as stated on the Completion Certificate.

The duration of the Final Performance Test shall be the 12-month period from the Date of Interim Completion as stated on the Certificate of Interim Completion.

The Contractor shall perform the Interim Performance Test and Final Performance Test for the entire PV plant.

For the purposes of the calculation of PRInterim and PRFinal and PV plant availabilities, measured data shall be restricted to periods where the measured global inclined irradiance is ≥ 50 W/m2.

Eligible Data Points

- Only data points that meet the validity criteria defined in the EPC Contract Schedule shall be considered eligible for the Performance Test evaluation.

For calculating the Performance Ratio for the Interim Performance Test and the Final Performance Test, all the periods of partial or total unavailability of the Facility shall be discarded from the calculation.

For sake of clarity, the Guaranteed Performance Ratio for the Interim Performance Test and the Final Performance Test shall not in any way be adjusted to account for tolerances, measurement errors or availability of the Facility or its systems.

Availability Test

During each year of the Interim Performance Test and Final Performance Test, the availability of the PV plant (AV) shall be equal to, or higher than, the Guaranteed Availability as dealt with under the EPC Contract.

Interim and Final Performance Test PR Calculation Methodology

The Interim Performance Test and Final Performance Test Performance Ratio (PR) calculations shall be carried out in accordance with the methodology defined in the relevant Schedule of the EPC Contract.

Requirements for Successful Completion of the Initial Performance Test

The Interim Performance Test and Final Performance Test will be considered as successfully completed if the conditions set in the EPC Contract are met.

Interim and Final Performance Test Reports

A test report shall be prepared and submitted to the Employer summarising the methodology, procedure, details and results of the test.

For each of Interim Performance Test and Final Performance Test, processed data shall be prepared in an Excel spreadsheet of 4 readings per hour (15-min reporting period) with the following columns:

Date and time;

Global inclined irradiance measured for each GII pyranometer;

Global inclined irradiance calculated mean value;

Ambient temperature measured for each ambient temperature sensor;

Ambient temperature calculated mean value;

Measured energy production measured at the revenue energy meter (meter output);

Performance Ratio (calculated);

Each string combiner box power;

Total inverter power; and

AV (calculated).

Each month of the test will be represented on a separate worksheet with a summary of data over the course of the month. An additional summary sheet will combine data over the whole Test Period.

The spreadsheet will be readable by the Employer for the purposes of auditing.

Final Acceptance Tests

In addition to the Final Performance Test the Contractor shall be responsible for completing and documenting the following Final Acceptance Tests to the satisfaction of the Employer. The Contractor will submit a Final Acceptance Test Plan (in accordance with the timing requirements in the Contract) to the Employer for the Employer’s comment and approval under the Contract.

Visual Inspection Tests

As a minimum the following parts shall be visually inspected for compliance with this specification and condition:

Trackers, including tracker motors and moving parts;

Fencing, gates and security system;

Inverters and inverter stations;

Pits, cabling, electrical boxes and protection devices;

Electrical installation including interconnections, protection equipment and utility interconnection equipment and associated housing structure;

Transformers;

Equipment labelling (confirm alignment with as-built drawings);

Monitoring system including meteorological stations and communications systems;

Health and safety signage;

Equipment storage conditions; and

Civil works (roads, footpaths, drains, trenches).

Functional Inspection Tests

The functional inspection test shall include verification of the correct functioning of: Emergency shutdown procedures;

Monitoring system including battery back-up, data buffering and communications;

Mains protection relay reset and restart;

Climate control equipment (air conditioners) in buildings;

Operation of security devices including locks, fencing, cameras, remote communications;

Monitoring of individual DC inputs at the inverter;

Correct operation of the metering equipment;

Pyranometers must be calibrated in accordance with the manufacturer's recommendations;

A competent and qualified third party shall conduct as a minimum the following tests;

Visual inspection of 100% of modules in accordance to IEC 61215. Any defects are to be recorded.

Thermal imaging of the site in accordance to IEC 62446 with the exception of PV modules;

IV curve testing on a sample of 10% of the strings per inverter to IEC62446. Strings will be selected by the Employer. Testing to be completed in stable conditions at least 200W/m2 prior to Provisional Acceptance. All records to include irradiation values;

10% of PV strings per inverter as selected by the Employer to undergo insulation resistance testing as per Test Method 1 and 2 of IEC 62446. Testing to be completed in stable conditions at least 200W/m2 prior to Final Acceptance. All records to include irradiation values; and

Insulation testing. All cables to be checked for proper insulation according to applicable Australian electrical regulations.

Tracker motors and associated electrical, control and communications equipment; and

Verifying satisfactory PV module tracker operation.

RINA Tech UK Ltd. Queensbury House 106 Queens Road Brighton, BN1 3XF, UK +44 (0)1273 819 429 rina.org.