## Introduction
Inspection and Test Plan
Project Name | Hessay | Project Number | EC006
Prepared By | Harry Crabb | Approved By
Revision | 0.1 | Date | 2026-06-10
SOLAR
01 Initial Site and Fencing
02 Trenching and Cables
03 Foundation Construction
04 Drainage
05 CCTV
06 Mounting Structure
07 Inverter and Isolator
08 Meteo and Weather Station
09 Transformer Station
>
X0A0T
X0A0T
X0A0T
>
>
>
>
>
>
>
>

## 01 Initial Site and Fencing
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
Compound Hardstanding
1 | P | Design review | Confirmation design layout meets ERs and planning requirements under the EPC contract. | Ethical Power | H |  |  | P | IFC drawings to be issued | Each IFC drawing
2 | M | Material review | Inspection and confirmation that materials meet the design specification. | Contractor | W |  |  | P MCHW 600 & 800 Series, BS EN 13242 | Material datasheets Material safety datasheets (if applicable) Material grading certificates EP-ITD-00-01 Material Delivery | All procured material
3 | M | Material delivery inspection | Confirmation that delivered material conforms to the design specification and the supplied documentation. | Contractor | W |  |  | P,V MCHW 600 & 800 Series, BS EN 13242 | EP-ITD-00-01 Material delivery | Each delivery of material
4 | C | Setting out | Inspection and confirmation of setting out. | Contractor | W |  |  | P,DI | EP-ITD-01-01 Setting out | Each compound area
5 | C | CBR testing | CBR ground testing | Contractor | H |  |  | TPI,P | CBR test certificates | 1 test every 25m2
6 | C | Compound Construction | Inspection and confirmation of compound construction | Contractor | W |  |  | V,DI MCHW 600 & 800 Series, BS EN 13242 | EP-ITD-01-02 Access Track/Compound Construction | 1 Inspection every 25m2
7 | C | Final dimensions and levels | Site engineer to take final dimension and level records | Contractor | S |  |  | DI | Site engineer DWG files | Each compound area
8 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each design
Access Tracks
1 | P | Design review | Confirmation design layout meets ERs and planning requirements under the EPC contract. | Ethical Power | H |  |  | P | IFC drawings to be issued | Each IFC drawing
2 | M | Material review | Inspection and confirmation that materials meet the design specification. | Contractor | W |  |  | P MCHW 600 & 800 Series, BS EN 13242 | Material datasheets Material safety datasheets (if applicable) Material grading certificates EP-ITD-00-01 Material Delivery | All procured material
3 | M | Material delivery inspection | Confirmation that delivered material conforms to the design specification and the supplied documentation. | Contractor | W |  |  | P,V MCHW 600 & 800 Series, BS EN 13242 | EP-ITD-00-01 Material delivery | Each delivery of material
4 | C | Setting out | Inspection and confirmation of setting out. | Contractor | W |  |  | P,DI | EP-ITD-01-01 Setting out | Each compound area
5 | C | CBR testing | CBR ground testing | Contractor | H |  |  | TPI,P | CBR test certificates | 1 test every 50m of track
6 | C | Compound Construction | Inspection and confirmation of compound construction | Contractor | W |  |  | V,DI MCHW 600 & 800 Series, BS EN 13242 | EP-ITD-01-02 Access Track/Compound Construction | 1 inspection for every 250m of access track
7 | C | Final dimensions and levels | Site engineer to take final dimension and level records | Contractor | S |  |  | DI | Site engineer DWG files | Each compound area
8 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each design
Deer Fencing and Gates
1 | P | Design review | Confirmation design layout meets ERs and planning requirements under the EPC contract. | Ethical Power | H |  |  | P | IFC drawings to be issued | Each IFC drawing
2 | M | Material review | Inspection and confirmation that materials meet the design specification. | Contractor | W |  |  | P | Material datasheets Material safety datasheets (if applicable) EP-ITD-00-01 Material Delivery | All procured material
3 | C | Setting out | Inspection and confirmation of setting out. | Contractor | W |  |  | P,DI | EP-ITD-01-01 Setting out | Each field fence line
4 | C | Deer fencing installation | Inspection of deer fencing installation | Contractor | S |  |  | P,DI | EP-ITD-01-04 Deer Fencing inspection | Every 500m fence line
5 | C | Access gate installation | Inspection of access gate installation | Contractor | S |  |  | P,DI | EP-ITD-01-05 Access Gate inspection | Each access gate
< BACK
X1A0T
X1A0T
X1A0T

## 02 Trenching and Cables
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
Cable trenching (ducted)
1 | P | Confirmation of trench route design | IFC drawings issued for trench route and elevations | EP |  |  |  | P | IFC Frawings
2 | M | Material documentation | Material documentation for - Ducts - Chambers - Cable - Connectors | Contractor | W |  |  | V | Material datasheets Safety datasheets Factory acceptance test documents Delivery notes EP-ITD-00-01 Material Delivery | All procured material
3 | C | Pre-installation cable testing | Cable sheath/IR testing prior to installation | Contractor | H |  |  | V,T | Test certificates | Each cable drum (AC LV, HV)
4 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | Complete trench route
5 | C | Trench installation inspection | Confirmation of trenching and duct installation | Contractor | W |  |  | V,DI | EP-ITD-02-01 Duct Trench installation | 1 inspection to be completed for every 150m of trench
6 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each trench route
Cable trenching (direct burial)
1 | P | Confirmation of trench route design | IFC drawings issued for trench route and elevations | EP |  |  |  | P | IFC Frawings
2 | M | Material documentation | Material documentation for - Ducts - Chambers - Cable - Connectors | Contractor | W |  |  | V | Material datasheets Safety datasheets Factory acceptance test documents Delivery notes EP-ITD-00-01 Material Delivery | All procured material
3 | C | Pre-installation cable testing | Cable sheath/IR testing prior to installation | Contractor | H |  |  | V,T | Test certificates | Each cable drum (AC LV, HV)
4 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | Complete trench route
5 | C | Trench installation inspection | Confirmation of trenching and duct installation | Contractor | W |  |  | V,DI | EP-ITD-02-06 Direct burial Trench installation | 1 inspection to be completed for every 150m of trench
6 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each trench route
Cable trenching (HV)
1 | P | Confirmation of trench route design | IFC drawings issued for trench route and elevations | EP |  |  |  | P | IFC Frawings
2 | M | Material documentation | Material documentation for - Ducts - Chambers - Cable - Connectors | Contractor | W |  |  | V | Material datasheets Safety datasheets Factory acceptance test documents Delivery notes EP-ITD-00-01 Material Delivery | All procured material
3 | C | Pre-installation cable testing | Cable sheath/IR testing prior to installation | Contractor | H |  |  | V,T | Test certificates | Each cable drum (AC LV, HV)
4 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | Complete trench route
5 | C | Trench installation inspection | Confirmation of trenching and duct installation | Contractor | W |  |  | V,DI | EP-ITD-02-06 Direct burial Trench installation | Every 100m of trench
6 | C | HV Cable pull inspection | Monitoring and inspection of HV cable pull | Contractor | W |  |  | V,DI | EP-ITD-08-01 HV Cable installation | 1 inspection to be completed for every 150m of trench
7 | C | HV Cable joint inspection (if required) | Inspection of HV Cable joint | Contractor | H |  |  | V | EP-ITD-08-05 Jointing termination record | 1 inspection for each joint or termination
8 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each trench route
Earthing
1 | P | Confirmation of trench route design | IFC drawings issued for trench route and elevations | EP |  |  |  | P | IFC Frawings
2 | M | Material documentation | Material documentation for - Cable - Crimps - Rods - Bolted connectors | Contractor | W |  |  | V | Material datasheets Safety datasheets Factory acceptance test documents Delivery notes EP-ITD-00-01 Material Delivery | All procured material
4 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | Complete trench route
5 | C | Trench installation inspection | Confirmation of trenching and duct installation | Contractor | W |  |  | V,DI | EP-ITD-02-06 Direct burial Trench installation | 1 inspection to be completed for every 150m of trench
6 | C | Exothermic/CAD Welding (where required) | Inspection of exothermic welded connection | Contractor | W |  |  | V | EP-ITD-05-02 Exothermic weld inspection | Each welded connection
7 | C | Ductor test | Ductor test for continuity across earth joints | Contractor | W |  |  | T | Photogrpahic evidence / test document | Each connection
8 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each trench route
Joint Bay
1 | P | Confirmation of trench route design | IFC drawings issued for trench route and elevations | EP |  |  |  | P | IFC Frawings
2 | M | Material documentation | Material documentation for - Cable - Joint Kits - Tooling | Contractor | W |  |  | V | Material datasheets Safety datasheets Factory acceptance test documents Delivery notes EP-ITD-00-01 Material Delivery | All procured material
3 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | Complete trench route
4 | C | Joint Bay installation & inspection | Inspection of joint bay installation prior to cable pull and jointing activities | Contractor | H |  |  | V | EP-ITD-02-04 Joint Bay Inspection | Each Joint Bay
5 | C | Cable joint installation & inspection | Inspection of the completed cable joints within a single bay | Contractor | H |  |  | V | EP-ITD-02-02 Jointing Termination Record | Each cable Joint
6 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each Joint Bay
< BACK
X1A0T
X1A0T
X1A0T

## 03 Foundation Construction
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
STS (MV Station) Foundations
1 | P | Design review | Confirmation design layout meets ERs and planning requirements under the EPC contract. | Ethical Power | H |  |  | P | IFC drawings to be issued | Each IFC drawing
2 | M | Material review | Inspection and confirmation that materials meet the design specification. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P EP-1528-STS-FS-1 | Material datasheets Material safety datasheets (if applicable) Material grading certificates | All procured material
3 | M | Material delivery inspection | Confirmation that delivered material conforms to the design specification and the supplied documentation. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P,V | EP-ITD-00-01 Material delivery | Each delivery of material
4 | C | Setting out | Inspection and confirmation of setting out activities | Contractor | W |  |  | P,DI | EP-ITD-01-01 Setting out | Each foundation
5 | C | Excavation | Confirmation of excavation condition and preparation | Contractor | W |  |  | V,DI | EP-ITD-01-07 Excavation/Earthworks | 1 inspection for each excavation
6 | C | Formation level CBR testing | CBR testing at formation level to confirm ground conditions meet minimum requirements for design installation | Contractor | H |  |  | TPI BS 1377-9: 2002 | CBR test certificates | Each foundation excavation
7 | C | Pre pour inspection | Confirmation of dimensions, reinfocement bar positioning, formwork condition, oiling/greasing, set in components, earthing | Contractor | W |  |  | V,DI | EP-ITD-04-01 Pre Pour check | Each concrete pour
8 | C | Pour monitoring | Confirmation of concrete specification, delivery documentation, weather conditions, pour progress, finish | Contractor | W |  |  | V | EP-ITD-04-02 Pour monitoring | Each concrete pour
9 | C | Cube and Slump testing | Complete slump test of delivered concrete to confirm conformance with design. Create concrete cubes for testing | Contractor | W |  |  | V,TPI Standard pass for slump. Cubes to be formed BS EN 12390-3:2019 for compressive strength tests Slump test BS EN 12350-2 |  | 1 slump per pour 4 test cubes (7 days, 14 days, 28 days, spare)
10 | C | Post pour inspection |  | Contractor | W |  |  | V,DI | EP-ITD-04-03 Post Pour check | Each concrete pour
11 | C | Cube test results | Confirmation concrete strength meets design requirements | Contractor | W |  |  | TPI Cubes to be formed BS EN 12390-3:2019 for compressive strength tests Slump test BS EN 12350-2 | Cube test certificates (UKAS test lab) | 4 test cubes (7 days, 14 days, 28 days, spare)
12 | C | Oil catchment bund sealant | Application and inspection of oil catchment bund expoy sealant | Contractor | W |  |  | V | Photo evidence | Each bund
13 | C | Oil catchment bund leak test | Oil catchment bund leak test | Contractor | W |  |  | V | EP-ITD-03-03 Transformer bund leak test | Test for each bund
14 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each design
CSS Foundation
1 | P | Design review | Confirmation design layout meets ERs and planning requirements under the EPC contract. | Ethical Power | H |  |  | P | IFC drawings to be issued | Each IFC drawing
2 | M | Material review | Inspection and confirmation that materials meet the design specification. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P EP-1528-STS-FS-1 | Material datasheets Material safety datasheets (if applicable) Material grading certificates | All procured material
3 | M | Material delivery inspection | Confirmation that delivered material conforms to the design specification and the supplied documentation. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P,V | EP-ITD-00-01 Material delivery | Each delivery of material
4 | C | Setting out | Inspection and confirmation of setting out activities | Contractor | W |  |  | P,DI | EP-ITD-01-01 Setting out | Each foundation
5 | C | Excavation | Confirmation of excavation condition and preparation | Contractor | W |  |  | V,DI | EP-ITD-01-07 Excavation/Earthworks | 1 inspection for each excavation
6 | C | Formation level CBR testing | CBR testing at formation level to confirm ground conditions meet minimum requirements for design installation | Contractor | H |  |  | TPI BS 1377-9: 2002 | CBR test certificates | Each foundation excavation
7 | C | Pre pour inspection | Confirmation of dimensions, reinfocement bar positioning, formwork condition, oiling/greasing, set in components, earthing | Contractor | W |  |  | V,DI | EP-ITD-04-01 Pre Pour check | Each concrete pour
8 | C | Pour monitoring | Confirmation of concrete specification, delivery documentation, weather conditions, pour progress, finish | Contractor | W |  |  | V | EP-ITD-04-02 Pour monitoring | Each concrete pour
9 | C | Cube and Slump testing | Complete slump test of delivered concrete to confirm conformance with design. Create concrete cubes for testing | Contractor | W |  |  | V,TPI Standard pass for slump. Cubes to be formed BS EN 12390-3:2019 for compressive strength tests Slump test BS EN 12350-2 |  | 1 slump per pour 4 test cubes (7 days, 14 days, 28 days, spare)
10 | C | Post pour inspection | Confirmation of dimensions, concrete finish, levels, line, set in components | Contractor | W |  |  | V,DI | EP-ITD-04-03 Post Pour check | Each concrete pour
11 | C | Cube test results | Confirmation concrete strength meets design requirements | Contractor | W |  |  | TPI Cubes to be formed BS EN 12390-3:2019 for compressive strength tests Slump test BS EN 12350-2 | Cube test certificates (UKAS test lab) | 4 test cubes (7 days, 14 days, 28 days, spare)
12 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each design
Minor Foundations
1 | P | Design review | Confirmation design layout meets ERs and planning requirements under the EPC contract. | Ethical Power | H |  |  | P | IFC drawings to be issued | Each IFC drawing
2 | M | Material review | Inspection and confirmation that materials meet the design specification. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P EP-1528-STS-FS-1 | Material datasheets Material safety datasheets (if applicable) Material grading certificates | All procured material
3 | M | Material delivery inspection | Confirmation that delivered material conforms to the design specification and the supplied documentation. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P,V | EP-ITD-00-01 Material delivery | Each delivery of material
4 | C | Setting out | Inspection and confirmation of setting out activities | Contractor | W |  |  | P,DI | EP-ITD-01-01 Setting out | Each foundation
5 | C | Excavation | Confirmation of excavation condition and preparation | Contractor | W |  |  | V,DI | EP-ITD-01-07 Excavation/Earthworks | 1 inspection for each excavation
6 | C | Post pour inspection |  | Contractor | W |  |  | V,DI | EP-ITD-04-03 Post Pour check | Each concrete pour
7 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each design
< BACK
X1A0T
X1A0T
X1A0T

## 04 Drainage
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
Trench filter drain
1 | P | Confirmation of trench route design | IFC drawings issued for trench route and elevations | EP |  |  |  | P | IFC Frawings
2 | M | Material documentation | Material documentation for - Ducts - Chambers - Connectors | Contractor | W |  |  | V | Material datasheets Safety datasheets Delivery notes EP-ITD-00-01 Material Delivery | All procured material
4 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | Complete trench route
5 | C | Drain installation inspection | Confirmation of trenching and duct installation | Contractor | W |  |  | V,DI | EP-ITD-03-01 Drainage | Every 150m of trench
6 | C | Manhole/Chamber inspection | Confirmation of manhole installation as per designs | Contractor | W |  |  | V,DI | EP-ITD-03-02 Manhole | Each manhole
7 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each trench route
< BACK
X1A0T
X1A0T
X1A0T

## 05 CCTV
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
CCTV Camera
1 | P | Design review | Confirmation design layout meets ERs and planning requirements under the EPC contract. | Ethical Power | H |  |  | P | IFC drawings to be issued | Each IFC drawing
2 | M | Material review | Inspection and confirmation that materials meet the design specification. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P EP-1528-STS-FS-1 | Material datasheets Material safety datasheets (if applicable) Material grading certificates | All procured material
3 | M | Material delivery inspection | Confirmation that delivered material conforms to the design specification and the supplied documentation. - Reinforcement bars - Waterstop materials - Set in materials (pipework, ducting) - Earthing materials - Chambers | Contractor | W |  |  | P,V | EP-ITD-00-01 Material delivery | Each delivery of material
4 | C | Setting out | Inspection and confirmation of setting out activities | Contractor | W |  |  | P,DI | EP-ITD-01-01 Setting out | Each foundation
5 | C | Excavation | Confirmation of excavation condition and preparation | Contractor | W |  |  | V,DI | EP-ITD-01-07 Excavation/Earthworks | 1 inspection for each excavation
6 | C | Final CCTV Base inspection |  | Contractor | W |  |  | V,DI | EP-ITD-14-01 CCTV Pole inspection | Each concrete pour
7 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each design
< BACK
X1A0T
X1A0T
X1A0T

## 07 Inverter and Isolator
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
String Inverter
1 | M | Material delivery inspection | Visual inspection of material condition on delivery. Confirmation that material spec meets design requirements | Contractor | W |  |  | V | EP-ITD-00-01 Material Delivery | Each delivery of material
2 | C | Inverter mounting installation inspection | Confirmation of Inverter mounitng structure and Inverter condition | Contractor | W |  |  | V,DI | EP-ITD-11-01 String Inverter Mounting Inspection | Each inverter (100%)
3 | C | Inverter termination inspection | Confirmation of Inverter LV AC and DC terminations | Contractor | W |  |  | V,DI | EP-ITD-11-02 String Inverter Terminations Inspection | Each inverter (100%)
4 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each field
LV AC Isolator
1 | M | Material delivery inspection | Visual inspection of material condition on delivery. Confirmation that material spec meets design requirements | Contractor | W |  |  | V | EP-ITD-00-01 Material Delivery | Each delivery of material
2 | C | LV AC Isolator mounting installation inspection | Confirmation of LV AC Isolator mounitng structure and Inverter condition | Contractor | W |  |  | V,DI | EP-ITD-12-01 AC Isolator Mounting Inspection | Each inverter (100%)
3 | C | LV AC Isolator termination inspection | Confirmation of LV AC terminations | Contractor | W |  |  | V,DI | EP-ITD-12-02 AC Isolator Installation Inspection | Each inverter (100%)
4 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each field
< BACK
X1A0T
X1A0T
X1A0T

## 06 Mounting Structure
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
Piling
1 | M | Material delivery inspection | Visual inspection of material condition on delivery. Confirmation that material spec meets design requirements | Contractor | W |  |  | V | EP-ITD-00-01 Material Delivery | Each delivery of material
2 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | 1x per field
3 | C | Piling installation inspection | Confirmation of pile installation as per manufactuer installation guidance | Contractor | W |  |  | V,DI | EP-ITD-10-01 Piling/Footing inspection | Each table (100%)
4 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each field
Mounting Structure
1 | M | Material delivery inspection | Visual inspection of material condition on delivery. Confirmation that material spec meets design requirements | Contractor | W |  |  | V | EP-ITD-00-01 Material Delivery | Each delivery of material
2 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | 1x per field
3 | C | Mounting Structure installation inspection | Confirmation of Mounting structure installation as per manufactuer installation guidance | Contractor | W |  |  | V,DI | EP-ITD-10-02 Mounting Strucutre inspection | Each table (100%)
4 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each field
PV Module mounting
1 | M | Material delivery inspection | Visual inspection of material condition on delivery. Confirmation that material spec meets design requirements | Contractor | W |  |  | V | EP-ITD-00-01 Material Delivery | Each delivery of material
2 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | 1x per field
3 | C | PV Module installation inspection | Confirmation of PV Module installation as per manufactuer installation guidance | Contractor | W |  |  | V,DI | EP-ITD-10-03 PV Module Mounting Inspection | Each table (100%)
4 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each field
< BACK
X1A0T
X1A0T
X1A0T

## 08 Meteo and Weather station
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  | Hessay |  | Project Number |  |  | EC006
ITP Scope |  |  | SOLAR
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
Weather Stations
1 | M | Material delivery inspection | Visual inspection of material condition on delivery. Confirmation that material spec meets design requirements | Contractor | W |  |  | V | EP-ITD-00-01 Material Delivery | Each delivery of material
2 | C | Setting out | Confirmation of setting out activities | Contractor | H |  |  | V,DI | EP-ITD-01-01 Setting out | 1x per field
3 | C | Wather station mounting installation | Confirmation of Mounting structure installation as per manufactuer installation guidance | Contractor | W |  |  | V,DI | EP-ITD-15-01 Meteo Station inspection | Each eather station (100%)
4 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Each field
< BACK
X1A0T
X1A0T
X1A0T

## 09 Transformer Station
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  |  |  | Project Number
ITP Scope
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
Transformer station housing
1 | M | Transformer station inspection on delivery | Visual inspection of the transformer station prior to landing and any installation works. | Contractor | W |  |  | V | EP-ITD-00-01 Material Delivery | Every transformer station
2 | C | Transformer station inspection on completion of installation | Visual inspection of the transformer station after installation works have been completed and prior to energisation. | Contractor, EP | H | W |  | V | EP-ITD-07-06 MV Station inspection | Every transformer station
3 | C | Redline & As-Built records | Handover of all redline marked up drawins to be added to as-built designs | Contractor | H |  |  | P | RL drawings | Every transformer station
HV Switchgear
1 | C | HV Cable terminations inspection | Inspection of HV terminations within each switchgear cabinet. | Contractor | H |  |  | V | EP-ITD-08-09 HV Cable termination to RMU or Switchgear | Every switchgear cabinet
2 | C | Switchgear pre-energisation inspection | Complete inspection of the switchgear and HV terminations prior to energisation. | Contractor, EP | H | W |  | V | EP-07-07 Switchgear Inspection | Every switchgear cabinet
LV Pillar
1 | C | LV Pillar pre-energisation inspection | Complete inspection of the LV Pillar terminations and components prior to energisation. | Contractor, EP | H | W |  | V | EP-07-08 LV Pillar inspection | Every LV Pillar
< BACK
X1A0T
X1A0T
X1A0T

## TEMPLATE (hidden)
Inspection and Test Plan | [8 empty] | Witness (W) - Opporunity shall be given to the required representatives to witness the works. Works can commence if no representative is present at the informed time Hold (H) - Works shall not proceed until works are witnessed by the required representatives Surveillance (S) - Works commence and will be witnessed on an ad-hoc basis
Project Name |  |  |  |  | Project Number
ITP Scope
Ref | Phase P = Pre works M = Material C = Construction | Element | Inspection/Test Description | Responsibility for Completion | Witness |  |  | Standard/Pass Criteria V = Visual DI = Dimension P = As per Project Drawings / Design TPI = Third Party Inspection T= Test | Evidence/Required Documentation | Frequency | Quantity for Project | Post Inspection/Test |  |  | file location (hyperlink) | Uploaded to SharePoint
[5 empty] | EPC | Client | DNO |  |  |  |  | Completed By | Date | Pass/Fail
< BACK
X1A0T
X1A0T
X1A0T